## Line
Arabic Line Name |  | English Line Name |  | Zone | Circuit Type | ID | KV | Line Conductor Type | Total Length [KM] | CT Ratio |  | Capacity |  |  | Equivelant Parameters | [13 empty] | Section 1 |  | Section 2 |  | Section 3 |  | Section4 |  | PSSE No. |  | Shunt |  | Online System Names |  |  | مهمات متصلة بالدائرة Mobiles | EMS Notes | Operation Notes | Planning Notes |  | Section 1 | [6 empty] | Section 2 | [6 empty] | Section 3 | [7 empty] | Section4
[12 empty] | Current Capacity |  | Designed | Parameters in P.U. [100 MVA Base] | [6 empty] | Parameters in Ohm and for B Mho | [6 empty] | Conductor Type | Length [KM] | Conductor Type | Length [KM] | Conductor Type | Length [KM] | Conductor Type | Length [KM] | [11 empty] | Parameters in P.U. [100 MVA Base] | [6 empty] | Parameters in P.U. [100 MVA Base] | [6 empty] | Parameters in P.U. [100 MVA Base] | [6 empty] | Parameters in P.U. [100 MVA Base]
From | To | From | To | [6 empty] | From | To | [A] | [MVA] | [A] | R1 | X1 | B1 | R0 | X0 | B0 | Xm | R1 | X1 | B1 | R0 | X0 | B0 | Xm | [8 empty] | Fr | To | Fr | To | Line Name | From Station | To Station |  |  |  |  | R1 | X1 | B1 | R0 | X0 | B0 | Xm | R1 | X1 | B1 | R0 | X0 | B0 | Xm | R1 | X1 | B1 | R0 | X0 | B0 | Xm | R1 | X1 | B1 | R0 | X0 | B0 | Xm
Data Entery | Data Entery | Data Entery | Data Entery | Data Entry | Data Entery | Data Entery | Data Entery | Equation | Equation | Data Entery | Data Entery | Data Entery | Equation | Data Entery | Equation | Equation | Equation | Equation | Equation | Equation | Equation | Equation from Lnlst | Equation from Lnlst | Equation from Lnlst | Equation from Lnlst | Equation from Lnlst | Equation from Lnlst | Equation from Lnlst | Data Entry | Data Entry | Data Entry | Data Entry | Data Entry | Data Entry | Data Entry | Data Entry |  |  | Data Entry | Data Entry |  |  |  | Data Entry | Data Entry | Data Entry | Data Entry
العين السخنة | الاقتصادية 2 | EIN-SOKHNA | EKTESADEYA_2 | القاهرة | Circuit | 1 | 500 | 3*506 AAAC | 24 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00020832 | 0.002832 | 0.2376 | 0.0023712 | 0.007488 | 0.1752 | 0.002208 | 0.5208 | 7.08 | 9.504e-05 | 5.928 | 18.72 | 7.008e-05 | 5.52 | 3*506 AAAC | 24 | [6 empty] | 18 |  | 0 | 0 |  | AIN_SKHN | [5 empty] | 0.00020832 | 0.002832 | 0.2376 | 0.0023712 | 0.007488 | 0.1752 | 0.002208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العين السخنة | الاقتصادية 2 | EIN-SOKHNA | EKTESADEYA_2 | القاهرة | Circuit | 2 | 500 | 3*506 AAAC | 24 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00020832 | 0.002832 | 0.2376 | 0.0023712 | 0.007488 | 0.1752 | 0.002208 | 0.5208 | 7.08 | 9.504e-05 | 5.928 | 18.72 | 7.008e-05 | 5.52 | 3*506 AAAC | 24 | [6 empty] | 18 |  | 0 | 0 |  | AIN_SKHN | [5 empty] | 0.00020832 | 0.002832 | 0.2376 | 0.0023712 | 0.007488 | 0.1752 | 0.002208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية 2 | العاصمة الادارية | EKTESADEYA_2 | NEW-CAPITAL | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR 3*506 AAAC | 63 | 3000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00054684 | 0.007434 | 0.6237 | 0.0062244 | 0.019656 | 0.4599 | 0.005796 | 1.3671 | 18.585 | 0.00024948 | 15.561 | 49.14 | 0.00018396 | 14.49 | 3*495/65 ACSR | 42 | 3*506 AAAC | 21 | [5 empty] | 21 | 0 | 0 |  |  | N_CAPITL |  |  |  |  | 0.00036456 | 0.004956 | 0.4158 | 0.0041496 | 0.013104 | 0.3066 | 0.003864 | 0.00018228 | 0.002478 | 0.2079 | 0.0020748 | 0.006552 | 0.1533 | 0.001932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية 2 | S1 | EKTESADEYA_2 | S1 | القاهرة | Circuit | 1 | 500 | 3*490/65 ACSR 3*506 AAAC | 77.7 | 3000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00067444 | 0.0091686 | 0.76923 | 0.0076768 | 0.024242 | 0.56721 | 0.0071484 | 1.6861 | 22.9215 | 0.00030769 | 19.1919 | 60.606 | 0.00022688 | 17.871 | 3*490/65 ACSR | 56.7 | 3*506 AAAC | 21 | [5 empty] | 35 | 0 | 0 |  |  | S1_CPTAL |  |  |  |  | 0.00049216 | 0.0066906 | 0.56133 | 0.005602 | 0.01769 | 0.41391 | 0.0052164 | 0.00018228 | 0.002478 | 0.2079 | 0.0020748 | 0.006552 | 0.1533 | 0.001932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاصمة الادارية | بدر | NEW-CAPITAL | BADR | القاهرة | Circuit | 1 | 500 | 4*495/65 ACSR | 34.214 | 2000/1 | 2000/1 | 2400 | 2078.4 | 2600 | 0.00023307 | 0.0037837 | 0.36106 | 0.0022509 | 0.011929 | 0.22732 | 0.002715 | 0.58266 | 9.4591 | 0.00014442 | 5.6273 | 29.8216 | 9.0926e-05 | 6.7875 | 4*495/65 ACSR | 34.214 | [6 empty] | 21 | 28 | 0 | 0 | A_BDR_CAP_1 | N_CAPITL | BADR |  | تم الاتصال بالمهندس وليد حسني من العاصمة الادارية وافاد ان كل محولات التيار للدوائر جهد 500 ك ف هي 1/2000 امبير وتم الاتصال يوم 23 من يونيو 2021 . و تم الاتصال ب م محمد يوسف من محطة بدر 500 وافاد ان كل محولات التيار لدوائر 500 ك ف هي 1/1000/2000 وتم اخيار 2000 امبير اي هي تتحمل 2000 امبير فقط ماعدا دوائر dc هي 1/2000/4000 وتم الاتصال في يوم 15 مارس 2021 |  |  | 0.00023307 | 0.0037837 | 0.36106 | 0.0022509 | 0.011929 | 0.22732 | 0.002715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاصمة الادارية | بدر | NEW-CAPITAL | BADR | القاهرة | Circuit | 2 | 500 | 4*495/65 ACSR | 34.214 | 2000/1 | 2000/1 | 2400 | 2078.4 | 2600 | 0.00023307 | 0.0037837 | 0.36106 | 0.0022509 | 0.011929 | 0.22732 | 0.002715 | 0.58266 | 9.4591 | 0.00014442 | 5.6273 | 29.8216 | 9.0926e-05 | 6.7875 | 4*495/65 ACSR | 34.214 | [6 empty] | 21 | 28 | 0 | 0 | A_BDR_CAP_2 | N_CAPITL | BADR |  |  |  |  | 0.00023307 | 0.0037837 | 0.36106 | 0.0022509 | 0.011929 | 0.22732 | 0.002715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
التبين 500 | العاصمة الادارية | TEBB.500 | NEW-CAPITAL | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR 3*506 AAAC | 42.042 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00036492 | 0.004961 | 0.41622 | 0.0041537 | 0.013117 | 0.30691 | 0.0038679 | 0.91231 | 12.4024 | 0.00016649 | 10.3844 | 32.7928 | 0.00012276 | 9.6697 | 3*495/65 ACSR | 34 | 3*506 AAAC | 8.042 |  |  |  |  | 9 | 21 | 0 | 0 | A_NCAPITL_TEPN | TBNPS500 | N_CAPITL |  |  |  |  | 0.00029512 | 0.004012 | 0.3366 | 0.0033592 | 0.010608 | 0.2482 | 0.003128 | 6.9805e-05 | 0.00094896 | 0.079616 | 0.00079455 | 0.0025091 | 0.058707 | 0.00073986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب القديمة | الغرب الجديدة | CAIRO-WST | CAIRO.W-NEW | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR | 1 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 8.68e-06 | 0.000118 | 0.0099 | 9.88e-05 | 0.000312 | 0.0073 | 9.2e-05 | 0.0217 | 0.295 | 3.96e-06 | 0.247 | 0.78 | 2.92e-06 | 0.23 | 3*495/65 ACSR | 1 | [6 empty] | 6 | 40 | 0 | 0 | A_CWETNEW_CW50 | CWEST500 | CWESTNEW |  |  |  |  | 8.68e-06 | 0.000118 | 0.0099 | 9.88e-05 | 0.000312 | 0.0073 | 9.2e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الغرب القديمة | CAIRO.500 | CAIRO-WST | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR | 16 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00013888 | 0.001888 | 0.1584 | 0.0015808 | 0.004992 | 0.1168 | 0.001472 | 0.3472 | 4.72 | 6.336e-05 | 3.952 | 12.48 | 4.672e-05 | 3.68 | 3*495/65 ACSR | 16 | [6 empty] | 5 | 6 | 0 | 0 | A_C500_CW50 | CAIRO500 | CWEST500 |  |  |  |  | 0.00013888 | 0.001888 | 0.1584 | 0.0015808 | 0.004992 | 0.1168 | 0.001472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | الغرب الجديدة | BASSOS | CAIRO.W-NEW | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR | 9 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 7.812e-05 | 0.001062 | 0.0891 | 0.0008892 | 0.002808 | 0.0657 | 0.000828 | 0.1953 | 2.655 | 3.564e-05 | 2.223 | 7.02 | 2.628e-05 | 2.07 | 3*495/65 ACSR | 9 | [6 empty] | 7 | 40 | 0 | 0 | A_CWESTNEW_BAS | BASSOUS | CWESTNEW |  | at bassous measure c.t 2000A and protection 1500 A |  |  | 7.812e-05 | 0.001062 | 0.0891 | 0.0008892 | 0.002808 | 0.0657 | 0.000828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
التبين 500 | الكريمات | TEBB.500 | KURAIMAT-I | القاهرة | Circuit | 1 | 500 | 3*490/65 ACSR | 76 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00065968 | 0.008968 | 0.7524 | 0.0075088 | 0.023712 | 0.5548 | 0.006992 | 1.6492 | 22.42 | 0.00030096 | 18.772 | 59.28 | 0.00022192 | 17.48 | 3*490/65 ACSR | 76 | [6 empty] | 9 | 10 | 0 | 0 | A_KRIM_TEB500 | TBNPS500 | KORIMAT |  |  |  |  | 0.00065968 | 0.008968 | 0.7524 | 0.0075088 | 0.023712 | 0.5548 | 0.006992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس غارب | غرب بكر | RAS.GHARB | WST.BAKR | القناة | Circuit | 1 | 500 | 4*506 AAAC | 30 | 2000/1 | 3000/1 | 2000 | 1732 | 3720 | 0.00020436 | 0.0033176 | 0.31659 | 0.0019737 | 0.010459 | 0.19932 | 0.0023806 | 0.5109 | 8.2941 | 0.00012664 | 4.9343 | 26.1486 | 7.9727e-05 | 5.9516 | 4*506 AAAC | 30 | [6 empty] | 32 | 41 | 0 | 0 | A_WBKR_RGHRB_1 | RS_GHARB | WBAKR |  | محول تيار |  |  | 0.00020436 | 0.0033176 | 0.31659 | 0.0019737 | 0.010459 | 0.19932 | 0.0023806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس غارب | غرب بكر | RAS.GHARB | WST.BAKR | القناة | Circuit | 2 | 500 | 4*506 AAAC | 30 | 2000/1 | 3000/1 | 2000 | 1732 | 3720 | 0.00020436 | 0.0033176 | 0.31659 | 0.0019737 | 0.010459 | 0.19932 | 0.0023806 | 0.5109 | 8.2941 | 0.00012664 | 4.9343 | 26.1486 | 7.9727e-05 | 5.9516 | 4*506 AAAC | 30 | [6 empty] | 32 | 41 | 0 | 0 | A_WBKR_RGHRB_2 | RS_GHARB | WBAKR |  | محول تيار |  |  | 0.00020436 | 0.0033176 | 0.31659 | 0.0019737 | 0.010459 | 0.19932 | 0.0023806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب بكر | لاكيلا | WST.BAKR | LEKELA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 25 | 2500/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 1.2475 | 7.65 | 8.125e-05 | 3.25 | 20.75 | 5.575e-05 | 14.75 | 2*405 AAAC | 25 | [6 empty] | 315 | 317 | 0 | 0 | B_WBKR_LEKLA_1 | WBAKR | LEKELA |  |  |  |  | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب بكر | لاكيلا | WST.BAKR | LEKELA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 25 | 2500/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 1.2475 | 7.65 | 8.125e-05 | 3.25 | 20.75 | 5.575e-05 | 14.75 | 2*405 AAAC | 25 | [6 empty] | 315 | 317 | 0 | 0 | B_WBKR_LEKLA_2 | WBAKR | LEKELA |  |  |  |  | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1 | S2 | S1 | S2 | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 5 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00013295 | 0.0017392 | 0.17332 | 0.0015882 | 0.0010845 | 0.1452 | 0 | 0.06435 | 0.84175 | 0.0003581 | 0.7687 | 0.5249 | 0.0003 | 0 | XLPE 2000mm2 Elswedy | 5 | [6 empty] | 445 | 449 | 0 | 0 | B_S1_CPTL_S2_1 | S1_CPTAL | S2_CPTAL |  |  |  |  | 0.00013295 | 0.0017392 | 0.17332 | 0.0015882 | 0.0010845 | 0.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1 | S2 | S1 | S2 | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 5 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00013295 | 0.0017392 | 0.17332 | 0.0015882 | 0.0010845 | 0.1452 | 0 | 0.06435 | 0.84175 | 0.0003581 | 0.7687 | 0.5249 | 0.0003 | 0 | XLPE 2000mm2 Elswedy | 5 | [6 empty] | 445 | 449 | 0 | 0 | B_S1_CPTL_S2_2 | S1_CPTAL | S2_CPTAL |  |  |  |  | 0.00013295 | 0.0017392 | 0.17332 | 0.0015882 | 0.0010845 | 0.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1 | S3 | S1 | S3 | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 8 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00021273 | 0.0027826 | 0.27731 | 0.0025412 | 0.0017352 | 0.23232 | 0 | 0.10296 | 1.3468 | 0.00057296 | 1.2299 | 0.83984 | 0.00048 | 0 | XLPE 2000mm2 Elswedy | 8 | [6 empty] | 445 | 447 | 0 | 0 | B_S1_CPTL_S3_1 | S1_CPTAL | S3_CPTAL |  |  |  |  | 0.00021273 | 0.0027826 | 0.27731 | 0.0025412 | 0.0017352 | 0.23232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1 | S3 | S1 | S3 | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 8 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00021273 | 0.0027826 | 0.27731 | 0.0025412 | 0.0017352 | 0.23232 | 0 | 0.10296 | 1.3468 | 0.00057296 | 1.2299 | 0.83984 | 0.00048 | 0 | XLPE 2000mm2 Elswedy | 8 | [6 empty] | 445 | 447 | 0 | 0 | B_S1_CPTL_S3_2 | S1_CPTAL | S3_CPTAL |  |  |  |  | 0.00021273 | 0.0027826 | 0.27731 | 0.0025412 | 0.0017352 | 0.23232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3 | S2 | S3 | S2 | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 3.5 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 9.3068e-05 | 0.0012174 | 0.12132 | 0.0011118 | 0.00075915 | 0.10164 | 0 | 0.045045 | 0.58922 | 0.00025067 | 0.53809 | 0.36743 | 0.00021 | 0 | XLPE 2000mm2 Elswedy | 3.5 | [6 empty] | 447 | 449 | 0 | 0 | B_S2_CPTL_S3_1 | S3_CPTAL | S2_CPTAL |  |  |  |  | 9.3068e-05 | 0.0012174 | 0.12132 | 0.0011118 | 0.00075915 | 0.10164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3 | S2 | S3 | S2 | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 3.5 | 2500/1 | 2500/1 | 1400 | 533.456 | 1400 | 9.3068e-05 | 0.0012174 | 0.12132 | 0.0011118 | 0.00075915 | 0.10164 | 0 | 0.045045 | 0.58922 | 0.00025067 | 0.53809 | 0.36743 | 0.00021 | 0 | XLPE 2000mm2 Elswedy | 3.5 | [6 empty] | 447 | 449 | 0 | 0 | B_S2_CPTL_S3_2 | S3_CPTAL | S2_CPTAL |  |  |  |  | 9.3068e-05 | 0.0012174 | 0.12132 | 0.0011118 | 0.00075915 | 0.10164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوزعبل | S1 | ABO-ZABAL | S1 | القاهرة | Circuit | 1 | 500 | 3*490/65 ACSR | 50.7 | 2000/1 | 3000/1 | 2000 | 1732 | 2790 | 0.00044008 | 0.0059826 | 0.50193 | 0.0050092 | 0.015818 | 0.37011 | 0.0046644 | 1.1002 | 14.9565 | 0.00020077 | 12.5229 | 39.546 | 0.00014804 | 11.661 | 3*490/65 ACSR | 50.7 | [6 empty] | 8 | 35 | 0 | 0 | A_S1_CPTL_AZBL | ABUZABAL | S1_CPTAL |  |  |  |  | 0.00044008 | 0.0059826 | 0.50193 | 0.0050092 | 0.015818 | 0.37011 | 0.0046644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاصمة الادارية | زهراء المعادي | NEW-CAPITAL | ZHRA.MAADI | القاهرة | Circuit | 1 | 500 | 4*490/65 ACSR | 33 | 2000/1 | 2000/1 | 2000 | 1732 | 2600 | 0.0002248 | 0.0036494 | 0.34825 | 0.0021711 | 0.011505 | 0.21925 | 0.0026187 | 0.56199 | 9.1235 | 0.0001393 | 5.4277 | 28.7635 | 8.77e-05 | 6.5467 | 4*490/65 ACSR | 33 | [6 empty] | 21 | 33 | 0 | 0 | A_NCAPTL_ZHRA1 | N_CAPITL | ZAHRAA_M |  | تم الاتصال بالمهندس وليد حسني من العاصمة الادارية وافاد ان كل محولات التيار للدوائر جهد 500 ك ف هي 1/2000 امبير وتم الاتصال يوم 23 من يونيو 2021 و محول تيار عند زهراء المعادي ايضا 1/2000 امبير |  |  | 0.0002248 | 0.0036494 | 0.34825 | 0.0021711 | 0.011505 | 0.21925 | 0.0026187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاصمة الادارية | زهراء المعادي | NEW-CAPITAL | ZHRA.MAADI | القاهرة | Circuit | 2 | 500 | 4*490/65 ACSR | 33 | 2000/1 | 2000/1 | 2000 | 1732 | 2600 | 0.0002248 | 0.0036494 | 0.34825 | 0.0021711 | 0.011505 | 0.21925 | 0.0026187 | 0.56199 | 9.1235 | 0.0001393 | 5.4277 | 28.7635 | 8.77e-05 | 6.5467 | 4*490/65 ACSR | 33 | [6 empty] | 21 | 33 | 0 | 0 | A_NCAPTL_ZHRA2 | N_CAPITL | ZAHRAA_M |  |  |  |  | 0.0002248 | 0.0036494 | 0.34825 | 0.0021711 | 0.011505 | 0.21925 | 0.0026187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب حلوان | زهراء المعادي | HELWAN | ZHRA.MAADI | القاهرة | Circuit | 1 | 500 | 3*495/65 ACSR | 121 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 2.6257 | 35.695 | 0.00047916 | 29.887 | 94.38 | 0.00035332 | 27.83 | 3*495/65 ACSR | 121 | [6 empty] | 23 | 33 | 0 | 0 | A_HELWN_ZHRAA1 | HELWAN_S | ZAHRAA_M |  |  |  |  | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب حلوان | زهراء المعادي | HELWAN | ZHRA.MAADI | القاهرة | Circuit | 2 | 500 | 3*495/65 ACSR | 121 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 2.6257 | 35.695 | 0.00047916 | 29.887 | 94.38 | 0.00035332 | 27.83 | 3*495/65 ACSR | 121 | [6 empty] | 23 | 33 | 0 | 0 | A_HELWN_ZHRAA2 | HELWAN_S | ZAHRAA_M |  |  |  |  | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | بدر | SUEZ-500 | BADR | القناة | Circuit | 1 | 500 | 3*490/65 ACSR | 67 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.00058156 | 0.007906 | 0.6633 | 0.0066196 | 0.020904 | 0.4891 | 0.006164 | 1.4539 | 19.765 | 0.00026532 | 16.549 | 52.26 | 0.00019564 | 15.41 | 3*490/65 ACSR | 67 | [6 empty] | 11 | 28 | 0 | 0 | A_BDR_SYZ500 | SUEZ_500 | BADR |  | تم الاتصال ب م محمد يوسف من محطة بدر 500 وافاد ان كل محولات التيار لدوائر 500 ك ف هي 1/1000/2000 وتم اخيار 2000 امبير اي هي تتحمل 2000 امبير فقط ماعدا دوائر dc هي 1/2000/4000 وتم الاتصال في يوم 15 مارس 2021 |  |  | 0.00058156 | 0.007906 | 0.6633 | 0.0066196 | 0.020904 | 0.4891 | 0.006164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوزعبل | بدر | ABO-ZABAL | BADR | القناة | Circuit | 1 | 500 | 3*490/65 ACSR | 53 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.00046004 | 0.006254 | 0.5247 | 0.0052364 | 0.016536 | 0.3869 | 0.004876 | 1.1501 | 15.635 | 0.00020988 | 13.091 | 41.34 | 0.00015476 | 12.19 | 3*490/65 ACSR | 53 | [6 empty] | 8 | 28 | 0 | 0 | A_BDR_ZABL | ABUZABAL | BADR |  |  |  |  | 0.00046004 | 0.006254 | 0.5247 | 0.0052364 | 0.016536 | 0.3869 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | عيون موسى | SUEZ-500 | O.MOUSA | القناة | Circuit | 1 | 500 | 3*490/65 ACSR | 23.7 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.00020572 | 0.0027966 | 0.23463 | 0.0023416 | 0.0073944 | 0.17301 | 0.0021804 | 0.51429 | 6.9915 | 9.3852e-05 | 5.8539 | 18.486 | 6.9204e-05 | 5.451 | 3*490/65 ACSR | 23.7 | [6 empty] | 11 | 12 | 0 | 0 | A_EMSA_SZ50_1 | SUEZ_500 | EIONMOSA |  |  |  |  | 0.00020572 | 0.0027966 | 0.23463 | 0.0023416 | 0.0073944 | 0.17301 | 0.0021804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عيون موسى | طابا | O.MOUSA | TABA | القناة | Circuit | 1 | 500 | 3*490/65 ACSR 3*506 AAAC | 244.169 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.0021194 | 0.028812 | 2.4173 | 0.024124 | 0.076181 | 1.7824 | 0.022464 | 5.2985 | 72.0299 | 0.00096691 | 60.3097 | 190.4518 | 0.00071297 | 56.1589 | 3*490/65 ACSR | 229.285 | 3*506 AAAC | 14.884 |  |  |  |  | 12 | 13 | -1 | -1 | A_EMSA_TABA | EIONMOSA | TABA |  |  |  |  | 0.0019902 | 0.027056 | 2.2699 | 0.022653 | 0.071537 | 1.6738 | 0.021094 | 0.00012919 | 0.0017563 | 0.14735 | 0.0014705 | 0.0046438 | 0.10865 | 0.0013693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طابا | الاردن | TABA | AQABA | القناة | Cable | 1 | 400 | XLPE1000HDPECABLE 3*506 AAAC | 32.3 | 1000/1 | 3000/1 | 1000 | 692.8 | 1000 | 0.00039202 | 0.0050326 | 1.3844 | 0.0043629 | 0.0098751 | 1.2166 | 0.0027313 | 0.62723 | 8.0522 | 0.00086526 | 6.9806 | 15.8002 | 0.00076038 | 4.37 | XLPE1000HDPECABLE | 13.3 | 3*506 AAAC | 19 |  |  |  |  | 95 | 97 | -1 | -1 | A_JORD_TABA | TABA | JORDAN |  | تم تغيير محول التيار جهة طابا من 1/2000 الى 1/1000 في 2010 , الخط الهوائي من طابا الى طويبة |  |  | 0.00013433 | 0.0015295 | 1.264 | 0.0014298 | 0.00061263 | 1.1278 | 0 | 0.00025769 | 0.0035031 | 0.12038 | 0.0029331 | 0.0092625 | 0.088768 | 0.0027313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | السويس الحرارية | SUEZ-500 | SUEZ-TH | القناة | Circuit | 1 | 500 | 3*506 AAAC | 15 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.0001302 | 0.00177 | 0.1485 | 0.001482 | 0.00468 | 0.1095 | 0.00138 | 0.3255 | 4.425 | 5.94e-05 | 3.705 | 11.7 | 4.38e-05 | 3.45 | 3*506 AAAC | 15 | [6 empty] | 11 | 20 | 0 | 0 | A_SZ500_SZTH_1 | SUEZ_500 | SUEZ_TH |  |  |  |  | 0.0001302 | 0.00177 | 0.1485 | 0.001482 | 0.00468 | 0.1095 | 0.00138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | السويس الحرارية | SUEZ-500 | SUEZ-TH | القناة | Circuit | 2 | 500 | 3*506 AAAC | 15 | 2000/1 | 2000/1 | 2000 | 1732 | 2790 | 0.0001302 | 0.00177 | 0.1485 | 0.001482 | 0.00468 | 0.1095 | 0.00138 | 0.3255 | 4.425 | 5.94e-05 | 3.705 | 11.7 | 4.38e-05 | 3.45 | 3*506 AAAC | 15 | [6 empty] | 11 | 20 | 0 | 0 | A_SZ500_SZTH_2 | SUEZ_500 | SUEZ_TH |  |  |  |  | 0.0001302 | 0.00177 | 0.1485 | 0.001482 | 0.00468 | 0.1095 | 0.00138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | كفر الزيات | BASSOS | KAFR.ZYAIT | وسط الدلتا | Circuit | 1 | 500 | 3*495/65 ACSR | 100 | 2000/1 | 2000/1 | 2000 | 1732 | 2200 | 0.000868 | 0.0118 | 0.99 | 0.00988 | 0.0312 | 0.73 | 0.0092 | 2.17 | 29.5 | 0.000396 | 24.7 | 78 | 0.000292 | 23 | 3*495/65 ACSR | 100 | [6 empty] | 7 | 17 | 0 | 0 | A_BASS_KZ50 | BASSOUS | KFZYT500 |  |  |  |  | 0.000868 | 0.0118 | 0.99 | 0.00988 | 0.0312 | 0.73 | 0.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوزعبل | كفر الزيات | ABO-ZABAL | KAFR.ZYAIT |  | Circuit | 1 | 500 | 3*495/65 ACSR | 119 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0010329 | 0.014042 | 1.1781 | 0.011757 | 0.037128 | 0.8687 | 0.010948 | 2.5823 | 35.105 | 0.00047124 | 29.393 | 92.82 | 0.00034748 | 27.37 | 3*495/65 ACSR | 119 | [6 empty] | 8 | 17 | 0 | 0 | A_AZAB_KZ50 | ABUZABAL | KFZYT500 |  | يتبع منطقة القاهرة 57 برج بطول 21 كم ومنطقة الدلتا 98 كم |  |  | 0.0010329 | 0.014042 | 1.1781 | 0.011757 | 0.037128 | 0.8687 | 0.010948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النوبارية | ابو المطامير | NOBARIA | A.MATAMR |  | Circuit | 1 | 500 | 3*490/65 ACSR | 76.5 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00066402 | 0.009027 | 0.75735 | 0.0075582 | 0.023868 | 0.55845 | 0.007038 | 1.6601 | 22.5675 | 0.00030294 | 18.8955 | 59.67 | 0.00022338 | 17.595 | 3*490/65 ACSR | 76.5 | [6 empty] | 14 | 29 | 0 | 0 | A_MTMR500_NBRI | NOBARIA | MATMR500 |  |  |  |  | 0.00066402 | 0.009027 | 0.75735 | 0.0075582 | 0.023868 | 0.55845 | 0.007038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سيدي كرير | ابو المطامير | SIDI-KRIR | A.MATAMR |  | Circuit | 1 | 500 | 3*490/65 ACSR 3*506 AAAC | 49.5 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00042966 | 0.005841 | 0.49005 | 0.0048906 | 0.015444 | 0.36135 | 0.004554 | 1.0741 | 14.6025 | 0.00019602 | 12.2265 | 38.61 | 0.00014454 | 11.385 | 3*490/65 ACSR | 16.75 | 3*506 AAAC | 32.75 |  |  |  |  | 15 | 29 | 0 | 0 | A_KRIR_MTMR500 | SEDKR500 | MATMR500 |  |  |  |  | 0.00014539 | 0.0019765 | 0.16583 | 0.0016549 | 0.005226 | 0.12227 | 0.001541 | 0.00028427 | 0.0038645 | 0.32422 | 0.0032357 | 0.010218 | 0.23908 | 0.003013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
أبو قير | كفر الزيات | ABO.KIR | KAFR.ZYAIT |  | Circuit | 1 | 500 | 3*490/65 ACSR 3*506 AAAC | 95.789 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00083145 | 0.011303 | 0.94831 | 0.009464 | 0.029886 | 0.69926 | 0.0088126 | 2.0786 | 28.2578 | 0.00037932 | 23.6599 | 74.7154 | 0.0002797 | 22.0315 | 3*490/65 ACSR | 34.26 | 3*506 AAAC | 61.529 |  |  |  |  | 16 | 17 | 0 | 0 | A_ABK_KFZ1 | ABK500 | KFZYT500 |  |  |  |  | 0.00029738 | 0.0040427 | 0.33917 | 0.0033849 | 0.010689 | 0.2501 | 0.0031519 | 0.00053407 | 0.0072604 | 0.60914 | 0.0060791 | 0.019197 | 0.44916 | 0.0056607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
أبو قير | كفر الزيات | ABO.KIR | KAFR.ZYAIT |  | Circuit | 2 | 500 | 3*490/65 ACSR 3*506 AAAC | 95.789 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00083145 | 0.011303 | 0.94831 | 0.009464 | 0.029886 | 0.69926 | 0.0088126 | 2.0786 | 28.2578 | 0.00037932 | 23.6599 | 74.7154 | 0.0002797 | 22.0315 | 3*490/65 ACSR | 34.26 | 3*506 AAAC | 61.529 |  |  |  |  | 16 | 17 | 0 | 0 | A_ABK_KFZ2 | ABK500 | KFZYT500 |  |  |  |  | 0.00029738 | 0.0040427 | 0.33917 | 0.0033849 | 0.010689 | 0.2501 | 0.0031519 | 0.00053407 | 0.0072604 | 0.60914 | 0.0060791 | 0.019197 | 0.44916 | 0.0056607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النوبارية | وادي النطرون | NOBARIA | WADI-NATRON |  | Circuit | 1 | 500 | 3*490/65 ACSR | 60 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0005208 | 0.00708 | 0.594 | 0.005928 | 0.01872 | 0.438 | 0.00552 | 1.302 | 17.7 | 0.0002376 | 14.82 | 46.8 | 0.0001752 | 13.8 | 3*490/65 ACSR | 60 | [6 empty] | 14 | 30 | 0 | 0 | A_W_NTRON_NBRI | NOBARIA | W_NATRON |  |  |  |  | 0.0005208 | 0.00708 | 0.594 | 0.005928 | 0.01872 | 0.438 | 0.00552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | وادي النطرون | CAIRO.500 | WADI-NATRON |  | Circuit | 1 | 500 | 3*490/65 ACSR | 58 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00050344 | 0.006844 | 0.5742 | 0.0057304 | 0.018096 | 0.4234 | 0.005336 | 1.2586 | 17.11 | 0.00022968 | 14.326 | 45.24 | 0.00016936 | 13.34 | 3*490/65 ACSR | 58 | [6 empty] | 5 | 30 | 0 | 0 | A_C500_W_NTRON | CAIRO500 | W_NATRON |  |  |  |  | 0.00050344 | 0.006844 | 0.5742 | 0.0057304 | 0.018096 | 0.4234 | 0.005336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | ايتاي | KAFR.ZYAIT | ETY-BARD |  | Circuit | 1 | 500 | 4*490/65 ACSR | 27.5 | 2000/1 | 2000/1 | 2000 | 1732 | 2600 | 0.00018733 | 0.0030412 | 0.29021 | 0.0018092 | 0.0095878 | 0.18271 | 0.0021822 | 0.46832 | 7.6029 | 0.00011608 | 4.5231 | 23.9696 | 7.3083e-05 | 5.4556 | 4*490/65 ACSR | 27.5 | [6 empty] | 17 | 26 | 0 | 0 | A_KZ50_ETY50_1 | KFZYT500 | ETAY500 |  | محول تيار |  |  | 0.00018733 | 0.0030412 | 0.29021 | 0.0018092 | 0.0095878 | 0.18271 | 0.0021822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | ايتاي | KAFR.ZYAIT | ETY-BARD |  | Circuit | 2 | 500 | 4*490/65 ACSR | 27.5 | 2000/1 | 2000/1 | 2000 | 1732 | 2600 | 0.00018733 | 0.0030412 | 0.29021 | 0.0018092 | 0.0095878 | 0.18271 | 0.0021822 | 0.46832 | 7.6029 | 0.00011608 | 4.5231 | 23.9696 | 7.3083e-05 | 5.4556 | 4*490/65 ACSR | 27.5 | [6 empty] | 17 | 26 | 0 | 0 | A_KZ50_ETY50_2 | KFZYT500 | ETAY500 |  | محول تيار |  |  | 0.00018733 | 0.0030412 | 0.29021 | 0.0018092 | 0.0095878 | 0.18271 | 0.0021822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | ابو المطامير | PROLOS | A.MATAMR |  | Circuit | 1 | 500 | 4*506 AAAC | 145 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00098774 | 0.016035 | 1.5302 | 0.0095396 | 0.050554 | 0.96337 | 0.011506 | 2.4693 | 40.0881 | 0.00061207 | 23.8489 | 126.3849 | 0.00038535 | 28.7658 | 4*506 AAAC | 145 | [6 empty] | 25 | 29 | 0 | 0 | A_MTMR_BROLOS1 | BURULLUS | MATMR500 |  |  |  |  | 0.00098774 | 0.016035 | 1.5302 | 0.0095396 | 0.050554 | 0.96337 | 0.011506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | ابو المطامير | PROLOS | A.MATAMR |  | Circuit | 2 | 500 | 4*506 AAAC | 145 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00098774 | 0.016035 | 1.5302 | 0.0095396 | 0.050554 | 0.96337 | 0.011506 | 2.4693 | 40.0881 | 0.00061207 | 23.8489 | 126.3849 | 0.00038535 | 28.7658 | 4*506 AAAC | 145 | [6 empty] | 25 | 29 | 0 | 0 | A_MTMR_BROLOS2 | BURULLUS | MATMR500 |  | محول تيار |  |  | 0.00098774 | 0.016035 | 1.5302 | 0.0095396 | 0.050554 | 0.96337 | 0.011506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو المطامير | وادي النطرون | A.MATAMR | WADI-NATRON |  | Circuit | 1 | 500 | 4*490/65 ACSR | 134.7 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00091758 | 0.014896 | 1.4215 | 0.0088619 | 0.046963 | 0.89494 | 0.010689 | 2.2939 | 37.2405 | 0.00056859 | 22.1548 | 117.4072 | 0.00035798 | 26.7225 | 4*490/65 ACSR | 134.7 | [6 empty] | 29 | 30 | 0 | 0 | A_MTMR_NATRON1 | MATMR500 | W_NATRON |  |  |  |  | 0.00091758 | 0.014896 | 1.4215 | 0.0088619 | 0.046963 | 0.89494 | 0.010689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو المطامير | وادي النطرون | A.MATAMR | WADI-NATRON |  | Circuit | 2 | 500 | 4*490/65 ACSR | 134.7 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00091758 | 0.014896 | 1.4215 | 0.0088619 | 0.046963 | 0.89494 | 0.010689 | 2.2939 | 37.2405 | 0.00056859 | 22.1548 | 117.4072 | 0.00035798 | 26.7225 | 4*490/65 ACSR | 134.7 | [6 empty] | 29 | 30 | 0 | 0 | A_MTMR_NATRON2 | MATMR500 | W_NATRON |  |  |  |  | 0.00091758 | 0.014896 | 1.4215 | 0.0088619 | 0.046963 | 0.89494 | 0.010689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو قير | تمي الامديد | ABO.KIR | TIMY.AMDID |  | Circuit | 1 | 500 | 3*506 AAAC 3*490/65 ACSR | 257 | 2000/1 | 3000/1 | 2000 | 1732 | 2200 | 0.0022308 | 0.030326 | 2.5443 | 0.025392 | 0.080184 | 1.8761 | 0.023644 | 5.5769 | 75.815 | 0.0010177 | 63.479 | 200.46 | 0.00075044 | 59.11 | 3*506 AAAC | 229 | 3*490/65 ACSR | 28 |  |  |  |  | 16 | 37 | 0 | 0 | A_ABK500_AMDED | ABK500 | T_AMADED |  |  |  |  | 0.0019877 | 0.027022 | 2.2671 | 0.022625 | 0.071448 | 1.6717 | 0.021068 | 0.00024304 | 0.003304 | 0.2772 | 0.0027664 | 0.008736 | 0.2044 | 0.002576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | تمي الامديد | BADR | TIMY.AMDID |  | Circuit | 1 | 500 | 3*506 AAAC 3*490/65 ACSR | 142.8 | 2000/1 | 3000/1 | 2000 | 1732 | 2790 | 0.0012395 | 0.01685 | 1.4137 | 0.014109 | 0.044554 | 1.0424 | 0.013138 | 3.0988 | 42.126 | 0.00056549 | 35.2716 | 111.384 | 0.00041698 | 32.844 | 3*506 AAAC | 114.8 | 3*490/65 ACSR | 28 |  |  |  |  | 28 | 37 | -1.65 | 0 | A_BDR_AMDED | BADR | T_AMADED |  |  |  |  | 0.00099646 | 0.013546 | 1.1365 | 0.011342 | 0.035818 | 0.83804 | 0.010562 | 0.00024304 | 0.003304 | 0.2772 | 0.0027664 | 0.008736 | 0.2044 | 0.002576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | ايتاي | PROLOS | ETY-BARD |  | Circuit | 1 | 500 | 3*506 AAAC | 106 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00092008 | 0.012508 | 1.0494 | 0.010473 | 0.033072 | 0.7738 | 0.009752 | 2.3002 | 31.27 | 0.00041976 | 26.182 | 82.68 | 0.00030952 | 24.38 | 3*506 AAAC | 106 | [6 empty] | 25 | 26 | 0 | 0 | A_ETAY_BROLOS1 | BURULLUS | ETAY500 |  |  |  |  | 0.00092008 | 0.012508 | 1.0494 | 0.010473 | 0.033072 | 0.7738 | 0.009752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | ايتاي | PROLOS | ETY-BARD |  | Circuit | 2 | 500 | 3*506 AAAC | 106 | 3000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.00092008 | 0.012508 | 1.0494 | 0.010473 | 0.033072 | 0.7738 | 0.009752 | 2.3002 | 31.27 | 0.00041976 | 26.182 | 82.68 | 0.00030952 | 24.38 | 3*506 AAAC | 106 | [6 empty] | 25 | 26 | 0 | 0 | A_ETAY_BROLOS2 | BURULLUS | ETAY500 |  |  |  |  | 0.00092008 | 0.012508 | 1.0494 | 0.010473 | 0.033072 | 0.7738 | 0.009752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | سمالوط | ASSYUT | SAMALUT | مصر الوسطي | Circuit | 1 | 500 | 3*482/70 ACSR | 141 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0012239 | 0.016638 | 1.3959 | 0.013931 | 0.043992 | 1.0293 | 0.012972 | 3.0597 | 41.595 | 0.00055836 | 34.827 | 109.98 | 0.00041172 | 32.43 | 3*482/70 ACSR | 141 | [6 empty] | 3 | 4 | 0 | 0 | A_AS50_SML5_1 | ASSUT500 | SMLUT500 |  |  |  |  | 0.0012239 | 0.016638 | 1.3959 | 0.013931 | 0.043992 | 1.0293 | 0.012972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | جنوب حلوان | ASSYUT | HELWAN | مصر الوسطي | Circuit | 1 | 500 | 3*490/65 ACSR | 221 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0019183 | 0.026078 | 2.1879 | 0.021835 | 0.068952 | 1.6133 | 0.020332 | 4.7957 | 65.195 | 0.00087516 | 54.587 | 172.38 | 0.00064532 | 50.83 | 3*490/65 ACSR | 221 | [6 empty] | 3 | 23 | -1 | -1 | A_AS50_HELWAN | ASSUT500 | HELWAN_S |  | الجزء الخاص بخطوط بني سويف في منطقة مصر الوسطى 71 كم والجزء الخاص بخطوط المنيا في منطقة مصر الوسطى 150 كم |  |  | 0.0019183 | 0.026078 | 2.1879 | 0.021835 | 0.068952 | 1.6133 | 0.020332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | جنوب حلوان | SAMALUT | HELWAN | مصر الوسطي | Circuit | 1 | 500 | 3*490/65 ACSR | 144 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0012499 | 0.016992 | 1.4256 | 0.014227 | 0.044928 | 1.0512 | 0.013248 | 3.1248 | 42.48 | 0.00057024 | 35.568 | 112.32 | 0.00042048 | 33.12 | 3*490/65 ACSR | 144 | [6 empty] | 4 | 23 | 0 | 0 | A_HELWAN_SMLUT | SMLUT500 | HELWAN_S |  | الجزء الخاص بخطوط بني سويف في منطقة مصر الوسطى 71 كم والجزء الخاص بخطوط المنيا في منطقة مصر الوسطى 73 كم |  |  | 0.0012499 | 0.016992 | 1.4256 | 0.014227 | 0.044928 | 1.0512 | 0.013248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | شمال الجيزة | SAMALUT | NRTH-GIZA | مصر الوسطي | Circuit | 1 | 500 | 3*482/70 ACSR 3*490/70 ACSR | 242 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0021006 | 0.028556 | 2.3958 | 0.02391 | 0.075504 | 1.7666 | 0.022264 | 5.2514 | 71.39 | 0.00095832 | 59.774 | 188.76 | 0.00070664 | 55.66 | 3*482/70 ACSR | 121 | 3*490/70 ACSR | 121 |  |  |  |  | 4 | 19 | 0 | 0 | A_GNTH_SML5 | SMLUT500 | GIZANRTH |  |  |  |  | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 0.0010503 | 0.014278 | 1.1979 | 0.011955 | 0.037752 | 0.8833 | 0.011132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | شمال الجيزة | CAIRO.500 | NRTH-GIZA | مصر الوسطي | Circuit | 1 | 500 | 3*490/65 ACSR | 28 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.00024304 | 0.003304 | 0.2772 | 0.0027664 | 0.008736 | 0.2044 | 0.002576 | 0.6076 | 8.26 | 0.00011088 | 6.916 | 21.84 | 8.176e-05 | 6.44 | 3*490/65 ACSR | 28 | [6 empty] | 5 | 19 | 0 | 0 | A_C500_GNTH | CAIRO500 | GIZANRTH |  |  |  |  | 0.00024304 | 0.003304 | 0.2772 | 0.0027664 | 0.008736 | 0.2044 | 0.002576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | الكريمات 1 | SAMALUT | KURAIMAT-I | مصر الوسطي | Circuit | 1 | 500 | 3*482/70 ACSR | 153.6 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0013332 | 0.018125 | 1.5206 | 0.015176 | 0.047923 | 1.1213 | 0.014131 | 3.3331 | 45.312 | 0.00060826 | 37.9392 | 119.808 | 0.00044851 | 35.328 | 3*482/70 ACSR | 153.6 | [6 empty] | 4 | 10 | 0 | 0 | A_KRIM_SML5 | SMLUT500 | KORIMAT |  |  |  |  | 0.0013332 | 0.018125 | 1.5206 | 0.015176 | 0.047923 | 1.1213 | 0.014131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الكريمات 1 | CAIRO.500 | KURAIMAT-I | مصر الوسطي | Circuit | 1 | 500 | 3*490/65 ACSR | 132 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0011458 | 0.015576 | 1.3068 | 0.013042 | 0.041184 | 0.9636 | 0.012144 | 2.8644 | 38.94 | 0.00052272 | 32.604 | 102.96 | 0.00038544 | 30.36 | 3*490/65 ACSR | 132 | [6 empty] | 5 | 10 | 0 | 0 | A_C500_KRIM | CAIRO500 | KORIMAT |  |  |  |  | 0.0011458 | 0.015576 | 1.3068 | 0.013042 | 0.041184 | 0.9636 | 0.012144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | غرب مغاغة | BANI-SWEF-G | MAGAGA-WST | مصر الوسطي | Circuit | 1 | 500 | 4*495/65 ACSR | 51.2 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.00034877 | 0.0056621 | 0.54031 | 0.0033684 | 0.017851 | 0.34017 | 0.0040629 | 0.87194 | 14.1553 | 0.00021612 | 8.4211 | 44.6269 | 0.00013607 | 10.1573 | 4*495/65 ACSR | 51.2 | [6 empty] | 22 | 24 | 0 | 0 | A_WMAGH_BENSG1 | BENSUIFG | W_MAGHAG |  |  |  |  | 0.00034877 | 0.0056621 | 0.54031 | 0.0033684 | 0.017851 | 0.34017 | 0.0040629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | غرب مغاغة | BANI-SWEF-G | MAGAGA-WST | مصر الوسطي | Circuit | 2 | 500 | 4*495/65 ACSR | 51.2 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.00034877 | 0.0056621 | 0.54031 | 0.0033684 | 0.017851 | 0.34017 | 0.0040629 | 0.87194 | 14.1553 | 0.00021612 | 8.4211 | 44.6269 | 0.00013607 | 10.1573 | 4*495/65 ACSR | 51.2 | [6 empty] | 22 | 24 | 0 | 0 | A_WMAGH_BENSG2 | BENSUIFG | W_MAGHAG |  |  |  |  | 0.00034877 | 0.0056621 | 0.54031 | 0.0033684 | 0.017851 | 0.34017 | 0.0040629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | شرق اسيوط | BANI-SWEF-G | EST.ASSUT | مصر الوسطي | Circuit | 1 | 500 | 4*490/65 ACSR | 194 | 2000/1 | 3000/1 | 2000 | 1732 | 2748 | 0.0013215 | 0.021454 | 2.0473 | 0.012763 | 0.067638 | 1.2889 | 0.015395 | 3.3038 | 53.6352 | 0.00081891 | 31.9082 | 169.0943 | 0.00051557 | 38.4867 | 4*490/65 ACSR | 194 | [6 empty] | 22 | 31 | 0 | 0 | A_ASSE_BSUF1 | BENSUIFG | ASUT_EST |  | محول تيار |  |  | 0.0013215 | 0.021454 | 2.0473 | 0.012763 | 0.067638 | 1.2889 | 0.015395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | شرق اسيوط | BANI-SWEF-G | EST.ASSUT | مصر الوسطي | Circuit | 2 | 500 | 4*490/65 ACSR | 194 | 2000/1 | 3000/1 | 2000 | 1732 | 2748 | 0.0013215 | 0.021454 | 2.0473 | 0.012763 | 0.067638 | 1.2889 | 0.015395 | 3.3038 | 53.6352 | 0.00081891 | 31.9082 | 169.0943 | 0.00051557 | 38.4867 | 4*490/65 ACSR | 194 | [6 empty] | 22 | 31 | 0 | 0 | A_ASSE_BSUF2 | BENSUIFG | ASUT_EST |  | محول تيار |  |  | 0.0013215 | 0.021454 | 2.0473 | 0.012763 | 0.067638 | 1.2889 | 0.015395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | راس غارب | SAMALUT | RAS.GHARB | القناة | Circuit | 1 | 500 | 3*490/65 ACSR | 247 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.002144 | 0.029146 | 2.4453 | 0.024404 | 0.077064 | 1.8031 | 0.022724 | 5.3599 | 72.865 | 0.00097812 | 61.009 | 192.66 | 0.00072124 | 56.81 | 3*490/65 ACSR | 247 | [6 empty] | 4 | 32 | -1.65 | -1.36 | A_GHARB_SMLT_1 | SMLUT500 | RS_GHARB |  | الجزء التابع لخطوط المنيا (مصر الوسطى) طوله 124 كم والجزء التابع للقناة 123 كم |  |  | 0.002144 | 0.029146 | 2.4453 | 0.024404 | 0.077064 | 1.8031 | 0.022724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | راس غارب | SAMALUT | RAS.GHARB | القناة | Circuit | 2 | 500 | 3*490/65 ACSR | 247 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.002144 | 0.029146 | 2.4453 | 0.024404 | 0.077064 | 1.8031 | 0.022724 | 5.3599 | 72.865 | 0.00097812 | 61.009 | 192.66 | 0.00072124 | 56.81 | 3*490/65 ACSR | 247 | [6 empty] | 4 | 32 | -1.65 | -1.36 | A_GHARB_SMLT_2 | SMLUT500 | RS_GHARB |  | الجزء التابع لخطوط المنيا (مصر الوسطى) طوله 124 كم والجزء التابع للقناة 123 كم |  |  | 0.002144 | 0.029146 | 2.4453 | 0.024404 | 0.077064 | 1.8031 | 0.022724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | بني سويف الصناعية | BANI-SWEF-G | INDS.BANISW | مصر الوسطي | Circuit | 1 | 500 | 4*490/65 ACSR | 33.5 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.0002282 | 0.0037047 | 0.35352 | 0.002204 | 0.01168 | 0.22257 | 0.0026584 | 0.57051 | 9.2617 | 0.00014141 | 5.5099 | 29.1993 | 8.9029e-05 | 6.6459 | 4*490/65 ACSR | 33.5 | [6 empty] | 22 | 38 | 0 | 0 | A_INSUF_BNSFG1 | BENSUIFG | IND_BNSF |  |  |  |  | 0.0002282 | 0.0037047 | 0.35352 | 0.002204 | 0.01168 | 0.22257 | 0.0026584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد بني سويف | بني سويف الصناعية | BANI-SWEF-G | INDS.BANISW | مصر الوسطي | Circuit | 2 | 500 | 4*490/65 ACSR | 33.5 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.0002282 | 0.0037047 | 0.35352 | 0.002204 | 0.01168 | 0.22257 | 0.0026584 | 0.57051 | 9.2617 | 0.00014141 | 5.5099 | 29.1993 | 8.9029e-05 | 6.6459 | 4*490/65 ACSR | 33.5 | [6 empty] | 22 | 38 | 0 | 0 | A_INSUF_BNSFG2 | BENSUIFG | IND_BNSF |  |  |  |  | 0.0002282 | 0.0037047 | 0.35352 | 0.002204 | 0.01168 | 0.22257 | 0.0026584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السد العالي | نجع حمادي الصناعية | HIGH.DAM | Industrial_NAG-HAM | مصر العليا | Circuit | 1 | 500 | 3*495/65 ACSR | 229 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.0019877 | 0.027022 | 2.2671 | 0.022625 | 0.071448 | 1.6717 | 0.021068 | 4.9693 | 67.555 | 0.00090684 | 56.563 | 178.62 | 0.00066868 | 52.67 | 3*495/65 ACSR | 229 | [6 empty] | 1 |  |  |  |  | HIGHDAM | [5 empty] | 0.0019877 | 0.027022 | 2.2671 | 0.022625 | 0.071448 | 1.6717 | 0.021068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السد العالي | نجع حمادي الصناعية | HIGH.DAM | Industrial_NAG-HAM | مصر العليا | Circuit | 2 | 500 | 3*495/65 ACSR | 229 | 2000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.0019877 | 0.027022 | 2.2671 | 0.022625 | 0.071448 | 1.6717 | 0.021068 | 4.9693 | 67.555 | 0.00090684 | 56.563 | 178.62 | 0.00066868 | 52.67 | 3*495/65 ACSR | 229 | [6 empty] | 1 |  |  |  |  | HIGHDAM | [5 empty] | 0.0019877 | 0.027022 | 2.2671 | 0.022625 | 0.071448 | 1.6717 | 0.021068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي الصناعية | نجع حمادي | Industrial_NAG-HAM | NAG-HAM | مصر العليا | Circuit | 1 | 500 | 3*495/65 ACSR | 7 | 3000/1 | 2000/1 | 2000 | 1732 | 2000 | 6.076e-05 | 0.000826 | 0.0693 | 0.0006916 | 0.002184 | 0.0511 | 0.000644 | 0.1519 | 2.065 | 2.772e-05 | 1.729 | 5.46 | 2.044e-05 | 1.61 | 3*495/65 ACSR | 7 | [7 empty] | 2 |  |  |  |  | NHMDI500 |  |  |  |  | 6.076e-05 | 0.000826 | 0.0693 | 0.0006916 | 0.002184 | 0.0511 | 0.000644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي الصناعية | نجع حمادي | Industrial_NAG-HAM | NAG-HAM | مصر العليا | Circuit | 2 | 500 | 3*495/65 ACSR | 7 | 3000/1 | 2000/1 | 2000 | 1732 | 2000 | 6.076e-05 | 0.000826 | 0.0693 | 0.0006916 | 0.002184 | 0.0511 | 0.000644 | 0.1519 | 2.065 | 2.772e-05 | 1.729 | 5.46 | 2.044e-05 | 1.61 | 3*495/65 ACSR | 7 | [7 empty] | 2 |  |  |  |  | NHMDI500 |  |  |  |  | 6.076e-05 | 0.000826 | 0.0693 | 0.0006916 | 0.002184 | 0.0511 | 0.000644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 3 | نجع حمادي الصناعية | BENBAN-3 | Industrial_NAG-HAM | مصر العليا | Circuit | 1 | 500 | 4*495/65 ACSR | 190 | 3150/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.0012943 | 0.021012 | 2.0051 | 0.0125 | 0.066243 | 1.2623 | 0.015077 | 3.2357 | 52.5293 | 0.00080202 | 31.2503 | 165.6078 | 0.00050494 | 37.6932 | 4*495/65 ACSR | 190 | [6 empty] | 46 |  |  |  |  | BENBAN_3 | [5 empty] | 0.0012943 | 0.021012 | 2.0051 | 0.0125 | 0.066243 | 1.2623 | 0.015077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 3 | نجع حمادي الصناعية | BENBAN-3 | Industrial_NAG-HAM | مصر العليا | Circuit | 2 | 500 | 4*495/65 ACSR | 190 | 3150/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.0012943 | 0.021012 | 2.0051 | 0.0125 | 0.066243 | 1.2623 | 0.015077 | 3.2357 | 52.5293 | 0.00080202 | 31.2503 | 165.6078 | 0.00050494 | 37.6932 | 4*495/65 ACSR | 190 | [6 empty] | 46 |  |  |  |  | BENBAN_3 | [5 empty] | 0.0012943 | 0.021012 | 2.0051 | 0.0125 | 0.066243 | 1.2623 | 0.015077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق سوهاج | نجع حمادي الصناعية | EST.SOHAG | Industrial_NAG-HAM | مصر العليا | Circuit | 2 | 500 | 4*495/65 ACSR | 226 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.0015395 | 0.024993 | 2.385 | 0.014869 | 0.078794 | 1.5015 | 0.017934 | 3.8488 | 62.4822 | 0.00095399 | 37.1714 | 196.9861 | 0.00060061 | 44.835 | 4*495/65 ACSR | 226 | [11 empty] | SOHG_EST | [5 empty] | 0.0015395 | 0.024993 | 2.385 | 0.014869 | 0.078794 | 1.5015 | 0.017934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 3 | توشكى 2 | BENBAN-3 | TOSHKA-2 | مصر العليا | Circuit | 1 | 500 | 3*490/65 ACSR | 255 | 3000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.0022134 | 0.03009 | 2.5245 | 0.025194 | 0.07956 | 1.8615 | 0.02346 | 5.5335 | 75.225 | 0.0010098 | 62.985 | 198.9 | 0.0007446 | 58.65 | 3*490/65 ACSR | 255 | [6 empty] | 46 | 47 | -1 | -1 | A_BENB3_TOSH1 | BENBAN_3 | TOSHK500 |  |  |  |  | 0.0022134 | 0.03009 | 2.5245 | 0.025194 | 0.07956 | 1.8615 | 0.02346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 3 | توشكى 2 | BENBAN-3 | TOSHKA-2 | مصر العليا | Circuit | 2 | 500 | 3*490/65 ACSR | 255 | 3000/1 | 3000/1 | 2000 | 1732 | 2000 | 0.0022134 | 0.03009 | 2.5245 | 0.025194 | 0.07956 | 1.8615 | 0.02346 | 5.5335 | 75.225 | 0.0010098 | 62.985 | 198.9 | 0.0007446 | 58.65 | 3*490/65 ACSR | 255 | [6 empty] | 46 | 47 | -1 | -1 | A_BENB3_TOSH2 | BENBAN_3 | TOSHK500 |  |  |  |  | 0.0022134 | 0.03009 | 2.5245 | 0.025194 | 0.07956 | 1.8615 | 0.02346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | اسيوط 500 | NAG-HAM | ASSYUT | مصر العليا | Circuit | 1 | 500 | 3*482/59.7 ACSR | 202 | 2000/1 | 2000/1 | 2000 | 1732 | 2000 | 0.0017534 | 0.023836 | 1.9998 | 0.019958 | 0.063024 | 1.4746 | 0.018584 | 4.3834 | 59.59 | 0.00079992 | 49.894 | 157.56 | 0.00058984 | 46.46 | 3*482/59.7 ACSR | 202 | [6 empty] | 2 | 3 | 0 | 0 | A_AS50_NH50_1 | NHMDI500 | ASSUT500 |  | مصر الوسطى 60 كم + في مصر العليا ( 90 كم قنا + 60 كم سوهاج ) |  |  | 0.0017534 | 0.023836 | 1.9998 | 0.019958 | 0.063024 | 1.4746 | 0.018584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الوليدية الجديدة | NAG-HAM | WALIDIA | مصر العليا | Circuit | 1 | 500 | 3*482/59.7 ACSR 3*490/65 ACSR | 193.5 | 2000/1 | 3150/1 | 2000 | 1732 | 2000 | 0.0016796 | 0.022833 | 1.9157 | 0.019118 | 0.060372 | 1.4125 | 0.017802 | 4.199 | 57.0825 | 0.00076626 | 47.7945 | 150.93 | 0.00056502 | 44.505 | 3*482/59.7 ACSR | 187.5 | 3*490/65 ACSR | 6 |  |  |  |  | 2 | 50 | 0 | 0 | A_NWALDIA_NH50 | NHMDI500 | N_WALDIA |  |  |  |  | 0.0016275 | 0.022125 | 1.8562 | 0.018525 | 0.0585 | 1.3687 | 0.01725 | 5.208e-05 | 0.000708 | 0.0594 | 0.0005928 | 0.001872 | 0.0438 | 0.000552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | الوليدية الجديدة | ASSYUT | WALIDIA | مصر الوسطي | Circuit | 1 | 500 | 3*482/59.7 ACSR 3*490/65 ACSR | 20.5 | 2000/1 | 3150/1 | 2000 | 1732 | 2000 | 0.00017794 | 0.002419 | 0.20295 | 0.0020254 | 0.006396 | 0.14965 | 0.001886 | 0.44485 | 6.0475 | 8.118e-05 | 5.0635 | 15.99 | 5.986e-05 | 4.715 | 3*482/59.7 ACSR | 14.5 | 3*490/65 ACSR | 6 |  |  |  |  | 3 | 50 | 0 | 0 | A_AS50_NWALDIA | ASSUT500 | N_WALDIA |  |  |  |  | 0.00012586 | 0.001711 | 0.14355 | 0.0014326 | 0.004524 | 0.10585 | 0.001334 | 5.208e-05 | 0.000708 | 0.0594 | 0.0005928 | 0.001872 | 0.0438 | 0.000552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | كفر الشيخ | PROLOS | K-SHEKH-NEW | وسط الدلتا | Circuit | 1 | 500 | 4*506 AAAC | 82.155 | 2000/1 | 3000/1 | 2000 | 1732 | 3000 | 0.00055964 | 0.0090854 | 0.86698 | 0.005405 | 0.028643 | 0.54583 | 0.0065193 | 1.3991 | 22.7134 | 0.00034679 | 13.5124 | 71.6079 | 0.00021833 | 16.2983 | 4*506 AAAC | 82.155 | [6 empty] | 25 | 48 | 0 | 0 | A_BRLS_KSHKH_1 | BURULLUS | N_KSHEKH |  | محول تيار |  |  | 0.00055964 | 0.0090854 | 0.86698 | 0.005405 | 0.028643 | 0.54583 | 0.0065193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البرلس | كفر الشيخ | PROLOS | K-SHEKH-NEW | وسط الدلتا | Circuit | 2 | 500 | 4*506 AAAC | 82.155 | 2000/1 | 3000/1 | 2000 | 1732 | 3000 | 0.00055964 | 0.0090854 | 0.86698 | 0.005405 | 0.028643 | 0.54583 | 0.0065193 | 1.3991 | 22.7134 | 0.00034679 | 13.5124 | 71.6079 | 0.00021833 | 16.2983 | 4*506 AAAC | 82.155 | [6 empty] | 25 | 48 | 0 | 0 | A_BRLS_KSHKH_2 | BURULLUS | N_KSHEKH |  | محول تيار |  |  | 0.00055964 | 0.0090854 | 0.86698 | 0.005405 | 0.028643 | 0.54583 | 0.0065193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمنود | كفر الشيخ | SAMANOD | K-SHEKH-NEW | وسط الدلتا | Circuit | 1 | 500 | 4*506 AAAC | 33.845 | 3000/1 | 3000/1 | 3000 | 2598 | 3000 | 0.00023055 | 0.0037429 | 0.35716 | 0.0022267 | 0.0118 | 0.22486 | 0.0026857 | 0.57638 | 9.3571 | 0.00014287 | 5.5667 | 29.5 | 8.9946e-05 | 6.7143 | 4*506 AAAC | 33.845 | [6 empty] | 36 | 48 | 0 | 0 | A_SMND_KSHKH_1 | SMNOD500 | N_KSHEKH |  |  |  |  | 0.00023055 | 0.0037429 | 0.35716 | 0.0022267 | 0.0118 | 0.22486 | 0.0026857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمنود | كفر الشيخ | SAMANOD | K-SHEKH-NEW | وسط الدلتا | Circuit | 2 | 500 | 4*506 AAAC | 33.845 | 3000/1 | 3000/1 | 3000 | 2598 | 3000 | 0.00023055 | 0.0037429 | 0.35716 | 0.0022267 | 0.0118 | 0.22486 | 0.0026857 | 0.57638 | 9.3571 | 0.00014287 | 5.5667 | 29.5 | 8.9946e-05 | 6.7143 | 4*506 AAAC | 33.845 | [6 empty] | 36 | 48 | 0 | 0 | A_SMND_KSHKH_2 | SMNOD500 | N_KSHEKH |  |  |  |  | 0.00023055 | 0.0037429 | 0.35716 | 0.0022267 | 0.0118 | 0.22486 | 0.0026857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | سمنود | EST.BANHA | SAMANOD | وسط الدلتا | Circuit | 1 | 500 | 4*506 AAAC | 80 | 3000/1 | 3000/1 | 3000 | 2598 | 3000 | 0.00054496 | 0.008847 | 0.84424 | 0.0052632 | 0.027892 | 0.53152 | 0.0063483 | 1.3624 | 22.1176 | 0.00033769 | 13.158 | 69.7296 | 0.00021261 | 15.8708 | 4*506 AAAC | 80 | [6 empty] | 27 | 36 | 0 | 0 | A_BNHA_SMNOD_1 | BANHA500 | SMNOD500 |  |  |  |  | 0.00054496 | 0.008847 | 0.84424 | 0.0052632 | 0.027892 | 0.53152 | 0.0063483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | سمنود | EST.BANHA | SAMANOD | وسط الدلتا | Circuit | 2 | 500 | 4*506 AAAC | 80 | 3000/1 | 3000/1 | 3000 | 2598 | 3000 | 0.00054496 | 0.008847 | 0.84424 | 0.0052632 | 0.027892 | 0.53152 | 0.0063483 | 1.3624 | 22.1176 | 0.00033769 | 13.158 | 69.7296 | 0.00021261 | 15.8708 | 4*506 AAAC | 80 | [6 empty] | 27 | 36 | 0 | 0 | A_BNHA_SMNOD_2 | BANHA500 | SMNOD500 |  |  |  |  | 0.00054496 | 0.008847 | 0.84424 | 0.0052632 | 0.027892 | 0.53152 | 0.0063483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النطرون | اكتوبر 500 | WADI-NATRON | OCTOBR.500 |  | Circuit | 1 | 500 | 4*490/65 ACSR | 48.48 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00033025 | 0.0053613 | 0.51161 | 0.0031895 | 0.016902 | 0.3221 | 0.0038471 | 0.82561 | 13.4033 | 0.00020464 | 7.9737 | 42.2561 | 0.00012884 | 9.6177 | 4*490/65 ACSR | 48.48 | [6 empty] | 30 | 49 | 0 | 0 | A_6OCT5_NTRN_1 | W_NATRON | N_OCT500 |  |  |  |  | 0.00033025 | 0.0053613 | 0.51161 | 0.0031895 | 0.016902 | 0.3221 | 0.0038471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النطرون | اكتوبر 500 | WADI-NATRON | OCTOBR.500 |  | Circuit | 2 | 500 | 4*490/65 ACSR | 48.48 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.00033025 | 0.0053613 | 0.51161 | 0.0031895 | 0.016902 | 0.3221 | 0.0038471 | 0.82561 | 13.4033 | 0.00020464 | 7.9737 | 42.2561 | 0.00012884 | 9.6177 | 4*490/65 ACSR | 48.48 | [6 empty] | 30 | 49 | 0 | 0 | A_6OCT5_NTRN_2 | W_NATRON | N_OCT500 |  |  |  |  | 0.00033025 | 0.0053613 | 0.51161 | 0.0031895 | 0.016902 | 0.3221 | 0.0038471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر 500 | غرب مغاغة | MAGAGA-WST | OCTOBR.500 | القاهرة | Circuit | 1 | 500 | 4*490/65 ACSR | 150.28 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.0010237 | 0.016619 | 1.5859 | 0.0098869 | 0.052395 | 0.99845 | 0.011925 | 2.5593 | 41.5479 | 0.00063436 | 24.7173 | 130.9871 | 0.00039938 | 29.8133 | 4*490/65 ACSR | 150.28 | [6 empty] | 24 | 49 | 0 | 0 | A_6OCT5_MAGH_1 | N_OCT500 | W_MAGHAG |  |  |  |  | 0.0010237 | 0.016619 | 1.5859 | 0.0098869 | 0.052395 | 0.99845 | 0.011925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر 500 | غرب مغاغة | MAGAGA-WST | OCTOBR.500 | القاهرة | Circuit | 2 | 500 | 4*490/65 ACSR | 150.28 | 3000/1 | 3000/1 | 2600 | 2251.6 | 2600 | 0.0010237 | 0.016619 | 1.5859 | 0.0098869 | 0.052395 | 0.99845 | 0.011925 | 2.5593 | 41.5479 | 0.00063436 | 24.7173 | 130.9871 | 0.00039938 | 29.8133 | 4*490/65 ACSR | 150.28 | [6 empty] | 24 | 49 | 0 | 0 | A_6OCT5_MAGH_2 | N_OCT500 | W_MAGHAG |  |  |  |  | 0.0010237 | 0.016619 | 1.5859 | 0.0098869 | 0.052395 | 0.99845 | 0.011925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق اسيوط | شرق سوهاج | EST.ASSUT | EST.SOHAG | مصر الوسطي | Circuit | 1 | 500 | 4*490/65 ACSR | 187 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.0012738 | 0.02068 | 1.9734 | 0.012303 | 0.065197 | 1.2424 | 0.014839 | 3.1846 | 51.6999 | 0.00078936 | 30.7568 | 162.9929 | 0.00049697 | 37.098 | 4*490/65 ACSR | 187 | [6 empty] | 31 | 42 | -1 | 0 | A_ASSE_SOHG1 | ASUT_EST | SOHG_EST |  |  |  |  | 0.0012738 | 0.02068 | 1.9734 | 0.012303 | 0.065197 | 1.2424 | 0.014839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق اسيوط | شرق سوهاج | EST.ASSUT | EST.SOHAG | مصر الوسطي | Circuit | 2 | 500 | 4*490/65 ACSR | 187 | 3000/1 | 3000/1 | 2748 | 2379.768 | 2748 | 0.0012738 | 0.02068 | 1.9734 | 0.012303 | 0.065197 | 1.2424 | 0.014839 | 3.1846 | 51.6999 | 0.00078936 | 30.7568 | 162.9929 | 0.00049697 | 37.098 | 4*490/65 ACSR | 187 | [6 empty] | 31 | 42 | -1 | 0 | A_ASSE_SOHG2 | ASUT_EST | SOHG_EST |  |  |  |  | 0.0012738 | 0.02068 | 1.9734 | 0.012303 | 0.065197 | 1.2424 | 0.014839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | باسوس | CAIRO-WST | BASSOS | القاهرة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 | 5.296 | 1100/1 | 3000/1 | 1100 | 419.144 | 1500 | 0.0012492 | 0.0048368 | 0.0066525 | 0.0037091 | 0.014034 | 0.0044634 | 0.0084886 | 0.60463 | 2.341 | 1.3745e-05 | 1.7952 | 6.7926 | 9.2219e-06 | 4.1085 | Thermal Stacir 1*238/97 | 5.296 | [6 empty] | 404 | 478 | 0 | 0 | B_BASS_CWST_1 | CAIROWST | BASSOUS |  | يوجد كابل على نزلات الدائرة XLPE1200 يحد تحميل الدائرة الى 950 امبير |  |  | 0.0012492 | 0.0048368 | 0.0066525 | 0.0037091 | 0.014034 | 0.0044634 | 0.0084886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | باسوس | CAIRO-WST | BASSOS | القاهرة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 | 5.296 | 1100/1 | 3000/1 | 1100 | 419.144 | 1500 | 0.0012492 | 0.0048368 | 0.0066525 | 0.0037091 | 0.014034 | 0.0044634 | 0.0084886 | 0.60463 | 2.341 | 1.3745e-05 | 1.7952 | 6.7926 | 9.2219e-06 | 4.1085 | Thermal Stacir 1*238/97 | 5.296 | [6 empty] | 404 | 478 | 0 | 0 | B_BASS_CWST_2 | CAIROWST | BASSOUS |  | محول تيار |  |  | 0.0012492 | 0.0048368 | 0.0066525 | 0.0037091 | 0.014034 | 0.0044634 | 0.0084886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | شبرا الخيمة | BASSOS | SHOBRA-KHMA | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 4 | 2000/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0.08 | 0.5376 | 0.000352 | 0.32 | 0.52 | 0.000264 | 0 | CableHi-Pr kanda1267 | 4 | [6 empty] | 478 | 480 | 0 | 0 | B_BASS_SHKH_1 | BASSOUS | SHOBRAKH |  |  |  |  | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | شبرا الخيمة | BASSOS | SHOBRA-KHMA | القاهرة | Cable | 2 | 220 | CableHi-Pr kanda1267 | 4 | 2000/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0.08 | 0.5376 | 0.000352 | 0.32 | 0.52 | 0.000264 | 0 | CableHi-Pr kanda1267 | 4 | [6 empty] | 478 | 480 | 0 | 0 | B_BASS_SHKH_2 | BASSOUS | SHOBRAKH |  |  |  |  | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | شبرا الخيمة | BASSOS | SHOBRA-KHMA | القاهرة | Cable | 3 | 220 | CableHi-Pr kanda1267 | 4 | 2000/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0.08 | 0.5376 | 0.000352 | 0.32 | 0.52 | 0.000264 | 0 | CableHi-Pr kanda1267 | 4 | [6 empty] | 478 | 480 | 0 | 0 | B_BASS_SHKH_3 | BASSOUS | SHOBRAKH |  |  |  |  | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | شبرا الخيمة | BASSOS | SHOBRA-KHMA | القاهرة | Cable | 4 | 220 | CableHi-Pr kanda1267 | 4 | 2000/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0.08 | 0.5376 | 0.000352 | 0.32 | 0.52 | 0.000264 | 0 | CableHi-Pr kanda1267 | 4 | [6 empty] | 478 | 480 | 0 | 0 | B_BASS_SHKH_4 | BASSOUS | SHOBRAKH |  |  |  |  | 0.00016529 | 0.0011107 | 0.17037 | 0.00066116 | 0.0010744 | 0.12778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | توليد الشمال | BASSOS | CAIRO.N-GEN | القاهرة | Cable | 1 | 220 | XLPE1200HDPECABLE | 8.85 | 3000/1 | 3150/1 | 950 | 361.988 | 950 | 0.00029549 | 0.0033645 | 0.25443 | 0.003145 | 0.0013476 | 0.22702 | 0 | 0.14302 | 1.6284 | 0.00052569 | 1.5222 | 0.65224 | 0.00046905 | 0 | XLPE1200HDPECABLE | 8.85 | [6 empty] | 446 | 448 | 0 | 0 | B_BASS_NCN_1 | BASSOUS | NCAIRON |  |  |  |  | 0.00029549 | 0.0033645 | 0.25443 | 0.003145 | 0.0013476 | 0.22702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | توليد الشمال | BASSOS | CAIRO.N-GEN | القاهرة | Cable | 2 | 220 | XLPE1200HDPECABLE | 8.85 | 3000/1 | 3150/1 | 950 | 361.988 | 950 | 0.00029549 | 0.0033645 | 0.25443 | 0.003145 | 0.0013476 | 0.22702 | 0 | 0.14302 | 1.6284 | 0.00052569 | 1.5222 | 0.65224 | 0.00046905 | 0 | XLPE1200HDPECABLE | 8.85 | [6 empty] | 446 | 448 | 0 | 0 | B_BASS_NCN_2 | BASSOUS | NCAIRON |  |  |  |  | 0.00029549 | 0.0033645 | 0.25443 | 0.003145 | 0.0013476 | 0.22702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | باسوس | HELUPLS | BASSOS | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR 2*240/44 ACO | 20 | 1600/1 | 3000/1 | 650 | 247.676 | 670 | 0.0023107 | 0.014264 | 0.032176 | 0.0065289 | 0.039256 | 0.021586 | 0.02438 | 1.1184 | 6.904 | 6.648e-05 | 3.16 | 19 | 4.46e-05 | 11.8 | 2*380/50 ACSR | 12 | 2*240/44 ACO | 8 |  |  |  |  | 444 | 446 | 0 | 0 | B_BASS_HELI_1 | HLIOPLIS | BASSOUS |  |  |  |  | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0.0012893 | 0.0067769 | 0.010571 | 0.0038017 | 0.015702 | 0.0086346 | 0.0097521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | باسوس | HELUPLS | BASSOS | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR 2*240/44 ACO | 20 | 1600/1 | 3000/1 | 650 | 247.676 | 670 | 0.0023107 | 0.014264 | 0.032176 | 0.0065289 | 0.039256 | 0.021586 | 0.02438 | 1.1184 | 6.904 | 6.648e-05 | 3.16 | 19 | 4.46e-05 | 11.8 | 2*380/50 ACSR | 12 | 2*240/44 ACO | 8 |  |  |  |  | 444 | 446 | 0 | 0 | B_BASS_HELI_2 | HLIOPLIS | BASSOUS |  |  |  |  | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0.0012893 | 0.0067769 | 0.010571 | 0.0038017 | 0.015702 | 0.0086346 | 0.0097521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | بهتيم | BASSOS | BAHTEM-I | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy energy | 7 | 3000/1 | 1200/1 | 1200 | 457.248 | 1400 | 0.00018614 | 0.0024348 | 0.24478 | 0.0022235 | 0.00092128 | 0.20328 | 0 | 0.09009 | 1.1784 | 0.00050575 | 1.0762 | 0.4459 | 0.00042 | 0 | XLPE 2000mm2 Elswedy energy | 7 | [6 empty] | 446 | 476 | 0 | 0 | B_BASS_BHTM_1 | BASSOUS | BAHTEEM |  |  |  |  | 0.00018614 | 0.0024348 | 0.24478 | 0.0022235 | 0.00092128 | 0.20328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | بهتيم | BASSOS | BAHTEM-I | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy energy | 7 | 3000/1 | 1200/1 | 1200 | 457.248 | 1400 | 0.00018614 | 0.0024348 | 0.24478 | 0.0022235 | 0.00092128 | 0.20328 | 0 | 0.09009 | 1.1784 | 0.00050575 | 1.0762 | 0.4459 | 0.00042 | 0 | XLPE 2000mm2 Elswedy energy | 7 | [6 empty] | 446 | 476 | 0 | 0 | B_BASS_BHTM_2 | BASSOUS | BAHTEEM |  |  |  |  | 0.00018614 | 0.0024348 | 0.24478 | 0.0022235 | 0.00092128 | 0.20328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | امبابة | CAIRO-WST | IMBABA | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 8.139 | 2500/1 | 1100/1 | 1100 | 419.144 | 1400 | 0.00021642 | 0.002831 | 0.28213 | 0.0025853 | 0.0017654 | 0.23636 | 0 | 0.10475 | 1.3702 | 0.00058292 | 1.2513 | 0.85443 | 0.00048834 | 0 | XLPE 2000mm2 Elswedy | 8.139 | [6 empty] | 402 | 405 | 0 | 0 | B_CWST_IMBAB_1 | IMBABA | CAIROWST |  | محول تيار |  |  | 0.00021642 | 0.002831 | 0.28213 | 0.0025853 | 0.0017654 | 0.23636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | امبابة | CAIRO-WST | IMBABA | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 8.139 | 2500/1 | 1100/1 | 1100 | 419.144 | 1400 | 0.00021642 | 0.002831 | 0.28213 | 0.0025853 | 0.0017654 | 0.23636 | 0 | 0.10475 | 1.3702 | 0.00058292 | 1.2513 | 0.85443 | 0.00048834 | 0 | XLPE 2000mm2 Elswedy | 8.139 | [6 empty] | 402 | 405 | 0 | 0 | B_CWST_IMBAB_2 | IMBABA | CAIROWST |  | محول تيار |  |  | 0.00021642 | 0.002831 | 0.28213 | 0.0025853 | 0.0017654 | 0.23636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | المعتمدية | CAIRO-WST | MOTAMDIA | القاهرة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*380/50 ACSR | 15 | 1100/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0021814 | 0.011096 | 0.023741 | 0.0062476 | 0.033565 | 0.014771 | 0.020588 | 1.0558 | 5.3702 | 4.9052e-05 | 3.0238 | 16.2456 | 3.0518e-05 | 9.9646 | Thermal Stacir 1*238/97 | 6 | 2*380/50 ACSR | 9 |  |  |  |  | 402 | 406 | 0 | 0 | B_CWST_MOTM_1 | CAIROWST | MOTAMDIA |  | محول تيار |  |  | 0.0014153 | 0.0054798 | 0.0075369 | 0.0042021 | 0.0159 | 0.0050567 | 0.009617 | 0.00076612 | 0.0056157 | 0.016204 | 0.0020455 | 0.017665 | 0.0097139 | 0.010971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغرب | المعتمدية | CAIRO-WST | MOTAMDIA | القاهرة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*380/50 ACSR | 15 | 1100/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0021814 | 0.011096 | 0.023741 | 0.0062476 | 0.033565 | 0.014771 | 0.020588 | 1.0558 | 5.3702 | 4.9052e-05 | 3.0238 | 16.2456 | 3.0518e-05 | 9.9646 | Thermal Stacir 1*238/97 | 6 | 2*380/50 ACSR | 9 |  |  |  |  | 402 | 406 | 0 | 0 | B_CWST_MOTM_2 | CAIROWST | MOTAMDIA |  | محول تيار |  |  | 0.0014153 | 0.0054798 | 0.0075369 | 0.0042021 | 0.0159 | 0.0050567 | 0.009617 | 0.00076612 | 0.0056157 | 0.016204 | 0.0020455 | 0.017665 | 0.0097139 | 0.010971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهرم | الجنوب | HARAM | CAIRO-SOTH | القاهرة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1200mm2 | 20.65 | 1600/1 | 2000/1 | 950 | 361.988 | 950 | 0.0017479 | 0.012206 | 0.13645 | 0.0057907 | 0.031507 | 0.10901 | 0.020784 | 0.84598 | 5.9077 | 0.00028193 | 2.8027 | 15.2495 | 0.00022522 | 10.0595 | 2*405 AAAC | 10 | 2*380/50 ACSR | 7.05 | XLPE 1200mm2 | 3.6 |  |  | 418 | 420 | 0 | 0 | B_NCS_NHRA | N_HARAM | N_CAIROS |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 0.00060012 | 0.004399 | 0.012693 | 0.0016023 | 0.013838 | 0.0076092 | 0.008594 | 0.00011678 | 0.0014846 | 0.10803 | 0.0015025 | 0.00052066 | 0.090605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجيزة | الجنوب | GIZA | CAIRO-SOTH | القاهرة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1200mm2 | 24.05 | 1600/1 | 2000/1 | 950 | 361.988 | 950 | 0.0018582 | 0.013608 | 0.23848 | 0.0072097 | 0.031999 | 0.19458 | 0.020784 | 0.89936 | 6.5863 | 0.00049273 | 3.4895 | 15.4875 | 0.00040202 | 10.0595 | 2*405 AAAC | 10 | 2*380/50 ACSR | 7.05 | XLPE 1200mm2 | 7 |  |  | 416 | 420 | 0 | 0 | B_GIZA_NCS | GIZA220 | N_CAIROS |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 0.00060012 | 0.004399 | 0.012693 | 0.0016023 | 0.013838 | 0.0076092 | 0.008594 | 0.00022707 | 0.0028868 | 0.21006 | 0.0029215 | 0.0010124 | 0.17618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجنوب | وادي حوف | CAIRO-SOTH | WADI-HOF | القاهرة | Circuit | 1 | 220 | 2*405 AAAC | 3.06 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00031548 | 0.0019346 | 0.0048134 | 0.0008219 | 0.0052475 | 0.0033027 | 0.0037302 | 0.15269 | 0.93636 | 9.945e-06 | 0.3978 | 2.5398 | 6.8238e-06 | 1.8054 | 2*405 AAAC | 3.06 | [6 empty] | 420 | 432 | 0 | 0 | B_NCS_WHOF_1 | N_CAIROS | WADIHOF |  |  |  |  | 0.00031548 | 0.0019346 | 0.0048134 | 0.0008219 | 0.0052475 | 0.0033027 | 0.0037302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجنوب | وادي حوف | CAIRO-SOTH | WADI-HOF | القاهرة | Circuit | 2 | 220 | 2*405 AAAC | 3.06 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00031548 | 0.0019346 | 0.0048134 | 0.0008219 | 0.0052475 | 0.0033027 | 0.0037302 | 0.15269 | 0.93636 | 9.945e-06 | 0.3978 | 2.5398 | 6.8238e-06 | 1.8054 | 2*405 AAAC | 3.06 | [6 empty] | 420 | 432 | 0 | 0 | B_NCS_WHOF_2 | N_CAIROS | WADIHOF |  |  |  |  | 0.00031548 | 0.0019346 | 0.0048134 | 0.0008219 | 0.0052475 | 0.0033027 | 0.0037302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | الجنوب | HADABA-I | CAIRO-SOTH | القاهرة | Circuit | 1 | 220 | Thermal Invar 1*255/88 | 30 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 3.425 | 13.2611 | 7.786e-05 | 10.1691 | 38.478 | 5.2239e-05 | 23.2732 | Thermal Invar 1*255/88 | 30 | [6 empty] | 408 | 420 | 0 | 0 | B_HDBA_NCS_1 | HADABA | N_CAIROS |  |  |  |  | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | الجنوب | HADABA-I | CAIRO-SOTH | القاهرة | Circuit | 2 | 220 | Thermal Invar 1*255/88 | 30 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 3.425 | 13.2611 | 7.786e-05 | 10.1691 | 38.478 | 5.2239e-05 | 23.2732 | Thermal Invar 1*255/88 | 30 | [6 empty] | 408 | 420 | 0 | 0 | B_HDBA_NCS_2 | HADABA | N_CAIROS |  |  |  |  | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجنوب | جنوب المعادي | CAIRO-SOTH | MAADY | القاهرة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 11.189 | 2000/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0026142 | 0.010166 | 0.014115 | 0.0077547 | 0.029474 | 0.0094746 | 0.017862 | 1.2653 | 4.9203 | 2.9163e-05 | 3.7533 | 14.2655 | 1.9576e-05 | 8.645 | Thermal Stacir 1*238/97 | 11 | 2*405 AAAC | 0.189 |  |  |  |  | 420 | 421 | 0 | 0 | B_MADI_S_NCS_1 | N_CAIROS | MAADI_S |  |  |  |  | 0.0025947 | 0.010046 | 0.013818 | 0.0077039 | 0.02915 | 0.0092706 | 0.017631 | 1.9486e-05 | 0.00011949 | 0.0002973 | 5.0764e-05 | 0.00032411 | 0.00020399 | 0.00023039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجنوب | جنوب المعادي | CAIRO-SOTH | MAADY | القاهرة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 11.189 | 2000/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0026142 | 0.010166 | 0.014115 | 0.0077547 | 0.029474 | 0.0094746 | 0.017862 | 1.2653 | 4.9203 | 2.9163e-05 | 3.7533 | 14.2655 | 1.9576e-05 | 8.645 | Thermal Stacir 1*238/97 | 11 | 2*405 AAAC | 0.189 |  |  |  |  | 420 | 421 | 0 | 0 | B_MADI_S_NCS_2 | N_CAIROS | MAADI_S |  |  |  |  | 0.0025947 | 0.010046 | 0.013818 | 0.0077039 | 0.02915 | 0.0092706 | 0.017631 | 1.9486e-05 | 0.00011949 | 0.0002973 | 5.0764e-05 | 0.00032411 | 0.00020399 | 0.00023039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عين الصيرة | زهراء المعادي | AINSERA | ZHRA.MAADI | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy Two Cable in Parralel of Cable L-Pr Brilli800 XLPE 1600mm2 Energya | 31.44 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1200 | 0.0017361 | 0.013829 | 0.91273 | 0.0087501 | 0.03904 | 0.71904 | 0.018773 | 0.84027 | 6.6934 | 0.0018858 | 4.235 | 18.8953 | 0.0014856 | 9.086 | 2*380/50 ACSR | 15.4 | XLPE 1600mm2 Elswedy | 2.83 | Two Cable in Parralel of Cable L-Pr Brilli800 | 7.5 | XLPE 1600mm2 Energya | 5.71 | 422 | 439 | 0 | 0 |  | EINSR220 | ZAHRAA_M |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 7.075e-05 | 0.00071042 | 0.060268 | 0.001201 | 0.00041748 | 0.072595 | 0 | 0.00017123 | 0.0014334 | 0.63888 | 0.0019137 | 0.0071281 | 0.47045 | 0 | 0.00018322 | 0.0020764 | 0.18585 | 0.0021354 | 0.0012671 | 0.15938 | 0
عين الصيرة | زهراء المعادي | AINSERA | ZHRA.MAADI | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy XLPE 1600mm2 Energya | 30.94 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1200 | 0.0017399 | 0.014153 | 0.42292 | 0.009807 | 0.032944 | 0.42816 | 0.018773 | 0.8421 | 6.8501 | 0.00087381 | 4.7466 | 15.9451 | 0.00088463 | 9.086 | 2*380/50 ACSR | 15.4 | XLPE 1600mm2 Elswedy | 9.83 | XLPE 1600mm2 Energya | 5.71 |  |  | 422 | 439 | 0 | 0 |  | EINSR220 | ZAHRAA_M |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 0.00024575 | 0.0024677 | 0.20934 | 0.0041717 | 0.0014501 | 0.25216 | 0 | 0.00018322 | 0.0020764 | 0.18585 | 0.0021354 | 0.0012671 | 0.15938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب المعادي | زهراء المعادي | MAADY | ZHRA.MAADI | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy XLPE 1600mm2 Energya | 22.93 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1200 | 0.0015392 | 0.012136 | 0.25167 | 0.0064107 | 0.031758 | 0.22255 | 0.018773 | 0.74497 | 5.8736 | 0.00051997 | 3.1028 | 15.371 | 0.00045982 | 9.086 | 2*380/50 ACSR | 15.4 | XLPE 1600mm2 Elswedy | 1.88 | XLPE 1600mm2 Energya | 5.65 |  |  | 421 | 439 | 0 | 0 |  | MAADI_S | ZAHRAA_M |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 4.7e-05 | 0.00047194 | 0.040036 | 0.00079783 | 0.00027734 | 0.048226 | 0 | 0.00018129 | 0.0020545 | 0.1839 | 0.0021129 | 0.0012537 | 0.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب المعادي | زهراء المعادي | MAADY | ZHRA.MAADI | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy XLPE 1600mm2 Energya | 22.93 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1200 | 0.0015392 | 0.012136 | 0.25167 | 0.0064107 | 0.031758 | 0.22255 | 0.018773 | 0.74497 | 5.8736 | 0.00051997 | 3.1028 | 15.371 | 0.00045982 | 9.086 | 2*380/50 ACSR | 15.4 | XLPE 1600mm2 Elswedy | 1.88 | XLPE 1600mm2 Energya | 5.65 |  |  | 421 | 439 | 0 | 0 |  | MAADI_S | ZAHRAA_M |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 4.7e-05 | 0.00047194 | 0.040036 | 0.00079783 | 0.00027734 | 0.048226 | 0 | 0.00018129 | 0.0020545 | 0.1839 | 0.0021129 | 0.0012537 | 0.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | اكتوبر | CAIRO.500 | 6-OCTOBR | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 28 | 1500/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 1.1536 | 8.456 | 0.00010416 | 3.08 | 26.6 | 6.244e-05 | 16.52 | 2*380/50 ACSR | 28 | [6 empty] | 400 | 410 | 0 | 0 | B_6_OC_C500_1 | CAIRO500 | 6_OCTBR |  |  |  |  | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | اكتوبر | CAIRO.500 | 6-OCTOBR | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR | 28 | 1500/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 1.1536 | 8.456 | 0.00010416 | 3.08 | 26.6 | 6.244e-05 | 16.52 | 2*380/50 ACSR | 28 | [6 empty] | 400 | 410 | 0 | 0 | B_6_OC_C500_2 | CAIRO500 | 6_OCTBR |  |  |  |  | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال اكتوبر | المطورين | OCT-NORTH | MOTAWREEN | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 1.45 | 1600/1 | 2000/1 | 1170 | 445.8168 | 1400 | 3.8557e-05 | 0.00050435 | 0.050263 | 0.00046058 | 0.00031451 | 0.042108 | 0 | 0.018661 | 0.24411 | 0.00010385 | 0.22292 | 0.15222 | 8.7e-05 | 0 | XLPE 2000mm2 Elswedy | 1.45 | [6 empty] | 412 | 461 | 0 | 0 |  | 6OCT_NTH | [5 empty] | 3.8557e-05 | 0.00050435 | 0.050263 | 0.00046058 | 0.00031451 | 0.042108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال اكتوبر | المطورين | OCT-NORTH | MOTAWREEN | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 1.45 | 1600/1 | 2000/1 | 1170 | 445.8168 | 1400 | 3.8557e-05 | 0.00050435 | 0.050263 | 0.00046058 | 0.00031451 | 0.042108 | 0 | 0.018661 | 0.24411 | 0.00010385 | 0.22292 | 0.15222 | 8.7e-05 | 0 | XLPE 2000mm2 Elswedy | 1.45 | [6 empty] | 412 | 461 | 0 | 0 |  | 6OCT_NTH | [5 empty] | 3.8557e-05 | 0.00050435 | 0.050263 | 0.00046058 | 0.00031451 | 0.042108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر | شمال اكتوبر | 6-OCTOBR | OCT-NORTH | القاهرة | Circuit | 1 | 220 | 2*380/88 ACSR | 11.6 | 1250/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00098744 | 0.007238 | 0.020886 | 0.0026364 | 0.022769 | 0.01252 | 0.01414 | 0.47792 | 3.5032 | 4.3152e-05 | 1.276 | 11.02 | 2.5868e-05 | 6.844 | 2*380/88 ACSR | 11.6 | [6 empty] | 410 | 412 | 0 | 0 | B_6OCN_6OCT_1 | 6_OCTBR | 6OCT_NTH |  |  |  |  | 0.00098744 | 0.007238 | 0.020886 | 0.0026364 | 0.022769 | 0.01252 | 0.01414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر 500 | شمال اكتوبر | OCTOBR.500 | OCT-NORTH | القاهرة | Circuit | 2 | 220 | 2*380/88 ACSR 3*380/50 ACSR Thermal Stacir 1*238/97 | 39.14 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.001771 | 0.023878 | 0.074963 | 0.019968 | 0.063174 | 0.055252 | 0.018731 | 0.85718 | 11.5571 | 0.00015488 | 9.6644 | 30.5763 | 0.00011416 | 9.0656 | 2*380/88 ACSR | 0.07 | 3*380/50 ACSR | 39 | Thermal Stacir 1*238/97 | 0.07 |  |  | 403 | 412 | 0 | 0 |  | N_OCT500 | 6OCT_NTH |  |  |  |  | 5.9587e-06 | 4.3678e-05 | 0.00012603 | 1.5909e-05 | 0.0001374 | 7.5552e-05 | 8.5331e-05 | 0.0017486 | 0.023771 | 0.074749 | 0.019903 | 0.062851 | 0.055118 | 0.018533 | 1.6512e-05 | 6.3931e-05 | 8.793e-05 | 4.9025e-05 | 0.0001855 | 5.8995e-05 | 0.0001122 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر 500 | اكتوبر | OCTOBR.500 | 6-OCTOBR | القاهرة | Circuit | 2 | 220 | 2*380/88 ACSR 3*380/50 ACSR Thermal Stacir 1*238/97 | 50.57 | 2000/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.002744 | 0.03101 | 0.095542 | 0.022566 | 0.085609 | 0.067589 | 0.032664 | 1.3281 | 15.0089 | 0.0001974 | 10.9217 | 41.4348 | 0.00013965 | 15.8093 | 2*380/88 ACSR | 11.5 | 3*380/50 ACSR | 39 | Thermal Stacir 1*238/97 | 0.07 |  |  | 403 | 410 | 0 | 0 |  | N_OCT500 | 6_OCTBR |  |  |  |  | 0.00097893 | 0.0071756 | 0.020706 | 0.0026136 | 0.022572 | 0.012412 | 0.014019 | 0.0017486 | 0.023771 | 0.074749 | 0.019903 | 0.062851 | 0.055118 | 0.018533 | 1.6512e-05 | 6.3931e-05 | 8.793e-05 | 4.9025e-05 | 0.0001855 | 5.8995e-05 | 0.0001122 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال اكتوبر | الشيخ زايد | OCT-NORTH | ZAID | القاهرة | Circuit | 1 | 220 | 2*380/88 ACSR | 15.4 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 0.63448 | 4.6508 | 5.7288e-05 | 1.694 | 14.63 | 3.4342e-05 | 9.086 | 2*380/88 ACSR | 15.4 | [6 empty] | 412 | 414 | 0 | 0 | B_6OCN_ZAYD_1 | 6OCT_NTH | ZAYD |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال اكتوبر | الشيخ زايد | OCT-NORTH | ZAID | القاهرة | Circuit | 2 | 220 | 2*380/88 ACSR | 15.4 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 0.63448 | 4.6508 | 5.7288e-05 | 1.694 | 14.63 | 3.4342e-05 | 9.086 | 2*380/88 ACSR | 15.4 | [6 empty] | 412 | 414 | 0 | 0 | B_6OCN_ZAYD_2 | 6OCT_NTH | ZAYD |  |  |  |  | 0.0013109 | 0.0096091 | 0.027727 | 0.0035 | 0.030227 | 0.016622 | 0.018773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب التبين | التبين 500 | SOTH.TEBBEN | TEBB.500 | القاهرة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 | 7.49 | 1600/1 | 2000/1 | 1200 | 457.248 | 1500 | 0.0017668 | 0.0068406 | 0.0094085 | 0.0052456 | 0.019849 | 0.0063124 | 0.012005 | 0.85511 | 3.3109 | 1.9439e-05 | 2.5389 | 9.6067 | 1.3042e-05 | 5.8106 | Thermal Stacir 1*238/97 | 7.49 | [6 empty] | 436 | 438 | 0 | 0 | B_NTEB_TBPS_1 | N_TEBBIN | TBNPS500 |  | سكاكين التبين لاتتحمل اكثر من 1200 امبير |  |  | 0.0017668 | 0.0068406 | 0.0094085 | 0.0052456 | 0.019849 | 0.0063124 | 0.012005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب التبين | التبين 500 | SOTH.TEBBEN | TEBB.500 | القاهرة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 | 7.49 | 1600/1 | 2000/1 | 1200 | 457.248 | 1500 | 0.0017668 | 0.0068406 | 0.0094085 | 0.0052456 | 0.019849 | 0.0063124 | 0.012005 | 0.85511 | 3.3109 | 1.9439e-05 | 2.5389 | 9.6067 | 1.3042e-05 | 5.8106 | Thermal Stacir 1*238/97 | 7.49 | [6 empty] | 436 | 438 | 0 | 0 | B_NTEB_TBPS_2 | N_TEBBIN | TBNPS500 |  | سكاكين التبين لاتتحمل اكثر من 1200 امبير |  |  | 0.0017668 | 0.0068406 | 0.0094085 | 0.0052456 | 0.019849 | 0.0063124 | 0.012005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عين الصيرة | البساتين | AINSERA | BASATEEN | القاهرة | Cable | 1 | 220 | XLPE1000mm2 | 4.3 | 1600/1 | 1200/1 | 924 | 352.081 | 924 | 0.00015636 | 0.0011017 | 0.11967 | 0.0018657 | 0.00071074 | 0.10406 | 0 | 0.07568 | 0.5332 | 0.00024725 | 0.903 | 0.344 | 0.000215 | 0 | XLPE1000mm2 | 4.3 | [6 empty] | 422 | 424 | 0 | 0 | B_BSTN_ES22_1 | EINSR220 | BASATEEN |  |  |  |  | 0.00015636 | 0.0011017 | 0.11967 | 0.0018657 | 0.00071074 | 0.10406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عين الصيرة | البساتين | AINSERA | BASATEEN | القاهرة | Cable | 2 | 220 | XLPE1000mm2 | 4.3 | 1600/1 | 1200/1 | 924 | 352.081 | 924 | 0.00015636 | 0.0011017 | 0.11967 | 0.0018657 | 0.00071074 | 0.10406 | 0 | 0.07568 | 0.5332 | 0.00024725 | 0.903 | 0.344 | 0.000215 | 0 | XLPE1000mm2 | 4.3 | [6 empty] | 422 | 424 | 0 | 0 | B_BSTN_ES22_2 | EINSR220 | BASATEEN |  |  |  |  | 0.00015636 | 0.0011017 | 0.11967 | 0.0018657 | 0.00071074 | 0.10406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
امبابة | الهضبة 1 | IMBABA | HADABA-I | القاهرة | Circuit & Cable | 1 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR XLPE 1600mm2 Elswedy | 31.5 | 2500/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.005426 | 0.023763 | 0.13356 | 0.017508 | 0.067404 | 0.13984 | 0.04059 | 2.6262 | 11.5015 | 0.00027595 | 8.4737 | 32.6233 | 0.00028894 | 19.6455 | Thermal Invar 1*255/88 | 20 | 2*380/50 ACSR | 7 | XLPE 1600mm2 Elswedy | 4.5 |  |  | 405 | 408 | 0 | 0 | B_HDBA_IMBA_1 | IMBABA | HADABA |  |  |  |  | 0.0047176 | 0.018266 | 0.025123 | 0.014007 | 0.053 | 0.016856 | 0.032057 | 0.00059587 | 0.0043678 | 0.012603 | 0.0015909 | 0.01374 | 0.0075552 | 0.0085331 | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
امبابة | الهضبة 1 | IMBABA | HADABA-I | القاهرة | Circuit & Cable | 2 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR XLPE 1600mm2 Elswedy | 31.5 | 2500/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.005426 | 0.023763 | 0.13356 | 0.017508 | 0.067404 | 0.13984 | 0.04059 | 2.6262 | 11.5015 | 0.00027595 | 8.4737 | 32.6233 | 0.00028894 | 19.6455 | Thermal Invar 1*255/88 | 20 | 2*380/50 ACSR | 7 | XLPE 1600mm2 Elswedy | 4.5 |  |  | 405 | 408 | 0 | 0 | B_HDBA_IMBA_2 | IMBABA | HADABA |  |  |  |  | 0.0047176 | 0.018266 | 0.025123 | 0.014007 | 0.053 | 0.016856 | 0.032057 | 0.00059587 | 0.0043678 | 0.012603 | 0.0015909 | 0.01374 | 0.0075552 | 0.0085331 | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
امبابة | المعتمدية | IMBABA | MOTAMDIA | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 4.5 | 2500/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0.05445 | 0.54675 | 0.000198 | 0.9243 | 0.3213 | 0.0002385 | 0 | XLPE 1600mm2 Elswedy | 4.5 | [6 empty] | 405 | 406 | 0 | 0 | B_IMBA_MOTM_1 | IMBABA | MOTAMDIA |  |  |  |  | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
امبابة | المعتمدية | IMBABA | MOTAMDIA | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 4.5 | 2500/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0.05445 | 0.54675 | 0.000198 | 0.9243 | 0.3213 | 0.0002385 | 0 | XLPE 1600mm2 Elswedy | 4.5 | [6 empty] | 405 | 406 | 0 | 0 | B_IMBA_MOTM_2 | IMBABA | MOTAMDIA |  |  |  |  | 0.0001125 | 0.0011296 | 0.095832 | 0.0019097 | 0.00066384 | 0.11543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سبتية 1 | الاستاد | SABTIA.I | STAD | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 10.5 | 1600/1 | 1200/1 | 1060 | 403.9024 | 1200 | 0.0002625 | 0.0026358 | 0.22361 | 0.004456 | 0.001549 | 0.26935 | 0 | 0.12705 | 1.2757 | 0.000462 | 2.1567 | 0.7497 | 0.0005565 | 0 | XLPE 1600mm2 Elswedy | 10.5 | [6 empty] | 456 | 468 | 0 | 0 | B_SBTI_ESTD_1 | SABTIA | ELESTAD |  |  |  |  | 0.0002625 | 0.0026358 | 0.22361 | 0.004456 | 0.001549 | 0.26935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محولات الشمال | سبتية 1 | CAIRO.NRTH | SABTIA.I | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 7.256 | 1500/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0001814 | 0.0018215 | 0.15452 | 0.0030793 | 0.0010704 | 0.18613 | 0 | 0.087798 | 0.8816 | 0.00031926 | 1.4904 | 0.51808 | 0.00038457 | 0 | XLPE 1600mm2 Elswedy | 7.256 | [6 empty] | 450 | 454 | 0 | 0 | B_CNTH_SBTI_1 | CAIRONTH | SABTIA |  |  |  |  | 0.0001814 | 0.0018215 | 0.15452 | 0.0030793 | 0.0010704 | 0.18613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محولات الشمال | سبتية 1 | CAIRO.NRTH | SABTIA.I | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 7.256 | 1500/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0001814 | 0.0018215 | 0.15452 | 0.0030793 | 0.0010704 | 0.18613 | 0 | 0.087798 | 0.8816 | 0.00031926 | 1.4904 | 0.51808 | 0.00038457 | 0 | XLPE 1600mm2 Elswedy | 7.256 | [6 empty] | 450 | 454 | 0 | 0 | B_CNTH_SBTI_2 | CAIRONTH | SABTIA |  |  |  |  | 0.0001814 | 0.0018215 | 0.15452 | 0.0030793 | 0.0010704 | 0.18613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محولات الشمال | شبرا الخيمة | CAIRO-NRTH | SHOBRA-KHMA | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 4.5 | 1500/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00018595 | 0.0012496 | 0.19166 | 0.0007438 | 0.0012087 | 0.14375 | 0 | 0.09 | 0.6048 | 0.000396 | 0.36 | 0.585 | 0.000297 | 0 | CableHi-Pr kanda1267 | 4.5 | [6 empty] | 452 | 480 | 0 | 0 | B_CNTH_SHKH | CAIRONTH | SHOBRAKH |  |  |  |  | 0.00018595 | 0.0012496 | 0.19166 | 0.0007438 | 0.0012087 | 0.14375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد الشمال | محولات الشمال | CAIRO.N-GEN | CAIRO.NRTH | القاهرة | Cable | 1 | 220 | Gas Insulated Busbar (Zero Branch) | 0.3 | 3150/1 | 3150/1 | 3000 | 1143.12 | 3000 | 9.7314e-06 | 0.00012372 | 0.0090024 | 0.00012521 | 4.3388e-05 | 0.0075504 | 0 | 0.00471 | 0.05988 | 1.86e-05 | 0.0606 | 0.021 | 1.56e-05 | 0 | Gas Insulated Busbar (Zero Branch) | 0.3 | [6 empty] | 448 | 450 | 0 | 0 | B_CNTH_NCN_1 | NCAIRON | CAIRONTH |  |  |  |  | 9.7314e-06 | 0.00012372 | 0.0090024 | 0.00012521 | 4.3388e-05 | 0.0075504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد الشمال | محولات الشمال | CAIRO.N-GEN | CAIRO.NRTH | القاهرة | Cable | 2 | 220 | Gas Insulated Busbar (Zero Branch) | 0.3 | 3150/1 | 3150/1 | 3000 | 1143.12 | 3000 | 9.7314e-06 | 0.00012372 | 0.0090024 | 0.00012521 | 4.3388e-05 | 0.0075504 | 0 | 0.00471 | 0.05988 | 1.86e-05 | 0.0606 | 0.021 | 1.56e-05 | 0 | Gas Insulated Busbar (Zero Branch) | 0.3 | [6 empty] | 448 | 450 | 0 | 0 | B_CNTH_NCN_2 | NCAIRON | CAIRONTH |  |  |  |  | 9.7314e-06 | 0.00012372 | 0.0090024 | 0.00012521 | 4.3388e-05 | 0.0075504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | توليد الشمال | HELUPLS | CAIRO.N-GEN | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy energy | 11.116 | 1600/1 | 3150/1 | 1250 | 476.3 | 1400 | 0.00029558 | 0.0038665 | 0.38872 | 0.0035309 | 0.001463 | 0.32281 | 0 | 0.14306 | 1.8714 | 0.00080313 | 1.709 | 0.70809 | 0.00066696 | 0 | XLPE 2000mm2 Elswedy energy | 11.116 | [6 empty] | 444 | 448 | 0 | 0 | B_HELI_NCN_1 | HLIOPLIS | NCAIRON |  |  |  |  | 0.00029558 | 0.0038665 | 0.38872 | 0.0035309 | 0.001463 | 0.32281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | توليد الشمال | HELUPLS | CAIRO.N-GEN | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy energy | 11.116 | 1600/1 | 3150/1 | 1250 | 476.3 | 1400 | 0.00029558 | 0.0038665 | 0.38872 | 0.0035309 | 0.001463 | 0.32281 | 0 | 0.14306 | 1.8714 | 0.00080313 | 1.709 | 0.70809 | 0.00066696 | 0 | XLPE 2000mm2 Elswedy energy | 11.116 | [6 empty] | 444 | 448 | 0 | 0 | B_HELI_NCN_2 | HLIOPLIS | NCAIRON |  |  |  |  | 0.00029558 | 0.0038665 | 0.38872 | 0.0035309 | 0.001463 | 0.32281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السبتية 1 | شبرا الخيمة | SABTIA.I | SHOBRA-KHMA | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 9 | 800/1 | 2000/1 | 800 | 304.832 | 1000 | 0.0003719 | 0.0024992 | 0.38333 | 0.0014876 | 0.0024174 | 0.2875 | 0 | 0.18 | 1.2096 | 0.000792 | 0.72 | 1.17 | 0.000594 | 0 | CableHi-Pr kanda1267 | 9 | [6 empty] | 456 | 480 | 0 | 0 | B_SBTI_SHKH_1 | SABTIA | SHOBRAKH |  | محول تيار |  |  | 0.0003719 | 0.0024992 | 0.38333 | 0.0014876 | 0.0024174 | 0.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السبتية 1 | شبرا الخيمة | SABTIA.I | SHOBRA-KHMA | القاهرة | Cable | 2 | 220 | CableHi-Pr kanda1267 | 9 | 800/1 | 2000/1 | 800 | 304.832 | 1000 | 0.0003719 | 0.0024992 | 0.38333 | 0.0014876 | 0.0024174 | 0.2875 | 0 | 0.18 | 1.2096 | 0.000792 | 0.72 | 1.17 | 0.000594 | 0 | CableHi-Pr kanda1267 | 9 | [6 empty] | 456 | 480 | 0 | 0 | B_SBTI_SHKH_2 | SABTIA | SHOBRAKH |  | محول تيار |  |  | 0.0003719 | 0.0024992 | 0.38333 | 0.0014876 | 0.0024174 | 0.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السبتية 1 | سبتية 2 | SABTIA.I | SABTIA.II | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 0.3 | 800/1 | 800/1 | 800 | 304.832 | 1000 | 1.2397e-05 | 8.3306e-05 | 0.012778 | 4.9587e-05 | 8.0579e-05 | 0.0095832 | 0 | 0.006 | 0.04032 | 2.64e-05 | 0.024 | 0.039 | 1.98e-05 | 0 | CableHi-Pr kanda1267 | 0.3 | [6 empty] | 454 | 458 | 0 | 0 | B_NSAB_SBTI_1 | SABTIA | N_SABTIA |  | محول تيار |  |  | 1.2397e-05 | 8.3306e-05 | 0.012778 | 4.9587e-05 | 8.0579e-05 | 0.0095832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السبتية 1 | سبتية 2 | SABTIA.I | SABTIA.II | القاهرة | Cable | 2 | 220 | CableHi-Pr kanda1267 | 0.3 | 800/1 | 800/1 | 800 | 304.832 | 1000 | 1.2397e-05 | 8.3306e-05 | 0.012778 | 4.9587e-05 | 8.0579e-05 | 0.0095832 | 0 | 0.006 | 0.04032 | 2.64e-05 | 0.024 | 0.039 | 1.98e-05 | 0 | CableHi-Pr kanda1267 | 0.3 | [6 empty] | 456 | 460 | 0 | 0 | B_NSAB_SBTI_2 | SABTIA | N_SABTIA |  | محول تيار |  |  | 1.2397e-05 | 8.3306e-05 | 0.012778 | 4.9587e-05 | 8.0579e-05 | 0.0095832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سبتية 2 | مترو رمسيس | SABTIA.II | MTRO-RAMSIS | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 1.6 | 1600/1 | 800/1 | 800 | 304.832 | 1000 | 6.6116e-05 | 0.0004443 | 0.068147 | 0.00026446 | 0.00042975 | 0.05111 | 0 | 0.032 | 0.21504 | 0.0001408 | 0.128 | 0.208 | 0.0001056 | 0 | CableHi-Pr kanda1267 | 1.6 | [6 empty] | 458 | 462 | 0 | 0 | B_MTRO_NSAB_1 | N_SABTIA | METRO |  | at metro ramses 800 A for diffrential and 1600 A for over cuurent |  |  | 6.6116e-05 | 0.0004443 | 0.068147 | 0.00026446 | 0.00042975 | 0.05111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سبتية 2 | مترو رمسيس | SABTIA.II | MTRO-RAMSIS | القاهرة | Cable | 2 | 220 | CableHi-Pr kanda1267 | 1.6 | 1600/1 | 800/1 | 800 | 304.832 | 1000 | 6.6116e-05 | 0.0004443 | 0.068147 | 0.00026446 | 0.00042975 | 0.05111 | 0 | 0.032 | 0.21504 | 0.0001408 | 0.128 | 0.208 | 0.0001056 | 0 | CableHi-Pr kanda1267 | 1.6 | [6 empty] | 460 | 464 | 0 | 0 | B_MTRO_NSAB_2 | N_SABTIA | METRO |  | at metro ramses 800 A for diffrential and 1600 A for over cuurent |  |  | 6.6116e-05 | 0.0004443 | 0.068147 | 0.00026446 | 0.00042975 | 0.05111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مترو رمسيس | الاستاد | MTRO-RAMSIS | STAD | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 8 | 1600/1 | 1200/1 | 1060 | 403.9024 | 1200 | 0.0002 | 0.0020083 | 0.17037 | 0.003395 | 0.0011802 | 0.20522 | 0 | 0.0968 | 0.972 | 0.000352 | 1.6432 | 0.5712 | 0.000424 | 0 | XLPE 1600mm2 Elswedy | 8 | [6 empty] | 464 | 468 | 0 | 0 | B_MTRO_STAD | METRO | ELESTAD |  | افاد م سليمان خاطررئيس قطاع مشروعات القاهرة ان تحميل الكابل 1090 امبير ( تم احلال الكبل القديم ) وهذا الكابل جديد |  |  | 0.0002 | 0.0020083 | 0.17037 | 0.003395 | 0.0011802 | 0.20522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مترو رمسيس | شبرا الخيمة | MTRO-RAMSIS | SHOBRA-KHMA | القاهرة | Cable | 1 | 220 | CableHi-Pr kanda1267 | 12 | 1600/1 | 2000/1 | 1000 | 381.04 | 1000 | 0.00049587 | 0.0033322 | 0.5111 | 0.0019835 | 0.0032231 | 0.38333 | 0 | 0.24 | 1.6128 | 0.001056 | 0.96 | 1.56 | 0.000792 | 0 | CableHi-Pr kanda1267 | 12 | [6 empty] | 464 | 480 | 0 | 0 | B_MTRO_SHKH | METRO | SHOBRAKH |  |  |  |  | 0.00049587 | 0.0033322 | 0.5111 | 0.0019835 | 0.0032231 | 0.38333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | الاستاد | CAIRO-EST | STAD | القاهرة | Cable | 1 | 220 | Cable Hi-Pr Dilion 1267 | 7 | 800/1 | 1200/1 | 800 | 304.832 | 1000 | 0.00040496 | 0.0018657 | 0.43639 | 0.0026277 | 0.004093 | 0.21954 | 0 | 0.196 | 0.903 | 0.00090164 | 1.2718 | 1.981 | 0.0004536 | 0 | Cable Hi-Pr Dilion 1267 | 7 | [6 empty] | 426 | 466 | 0 | 0 | B_CEST_STAD_1 | CAIROEST | ELESTAD |  | محول تيار |  |  | 0.00040496 | 0.0018657 | 0.43639 | 0.0026277 | 0.004093 | 0.21954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | مترو العباسية | CAIRO-EST | MERO-ABASIA | القاهرة | Cable | 1 | 220 | Giza XLPE 1200 | 11.3 | 800/1 | 1600/1 | 800 | 304.832 | 950 | 0.00037822 | 0.0042025 | 0.3316 | 0.0054049 | 0.001667 | 0.3544 | 0 | 0.18306 | 2.034 | 0.00068512 | 2.616 | 0.80682 | 0.00073224 | 0 | Giza XLPE 1200 | 11.3 | [6 empty] | 426 | 470 | 0 | 0 | B_CEST_NMTR | CAIROEST | NMETRO |  | محول تيار |  |  | 0.00037822 | 0.0042025 | 0.3316 | 0.0054049 | 0.001667 | 0.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاستاد | مترو العباسية | STAD | MERO-ABASIA | القاهرة | Cable | 1 | 220 | Giza XLPE 1200 | 3.3 | 1200/1 | 1600/1 | 950 | 361.988 | 950 | 0.00011045 | 0.0012273 | 0.096838 | 0.0015784 | 0.00048682 | 0.1035 | 0 | 0.05346 | 0.594 | 0.00020008 | 0.76395 | 0.23562 | 0.00021384 | 0 | Giza XLPE 1200 | 3.3 | [6 empty] | 466 | 470 | 0 | 0 | B_NMTR_STAD | ELESTAD | NMETRO |  |  |  |  | 0.00011045 | 0.0012273 | 0.096838 | 0.0015784 | 0.00048682 | 0.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عين الصيرة | منشية ناصر | AINSERA | MAN.NASER | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 | 5 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0.0785 | 0.998 | 0.00031 | 1.01 | 0.35 | 0.00026 | 0 | XLPE 1200mm2 | 5 | [6 empty] | 422 | 471 | 0 | 0 | B_ES22_MNASR_1 | EINSR220 | MAN_NASR |  |  |  |  | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عين الصيرة | منشية ناصر | AINSERA | MAN.NASER | القاهرة | Cable | 2 | 220 | XLPE 1200mm2 | 5 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0.0785 | 0.998 | 0.00031 | 1.01 | 0.35 | 0.00026 | 0 | XLPE 1200mm2 | 5 | [6 empty] | 422 | 471 | 0 | 0 | B_ES22_MNASR_2 | EINSR220 | MAN_NASR |  |  |  |  | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مترو العباسية | منشية ناصر | MERO-ABASIA | MAN.NASER | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 | 5 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0.0785 | 0.998 | 0.00031 | 1.01 | 0.35 | 0.00026 | 0 | XLPE 1200mm2 | 5 | [6 empty] | 470 | 471 | 0 | 0 | B_MNASR_NMTR_1 | NMETRO | MAN_NASR |  |  |  |  | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مترو العباسية | منشية ناصر | MERO-ABASIA | MAN.NASER | القاهرة | Cable | 2 | 220 | XLPE 1200mm2 | 5 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0.0785 | 0.998 | 0.00031 | 1.01 | 0.35 | 0.00026 | 0 | XLPE 1200mm2 | 5 | [6 empty] | 470 | 471 | 0 | 0 | B_MNASR_NMTR_2 | NMETRO | MAN_NASR |  |  |  |  | 0.00016219 | 0.002062 | 0.15004 | 0.0020868 | 0.00072314 | 0.12584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | الشرق | HELUPLS | CAIRO-EST | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 | 12.6 | 1600/1 | 800/1 | 800 | 304.832 | 950 | 0.00040872 | 0.0051962 | 0.3781 | 0.0052587 | 0.0018223 | 0.31712 | 0 | 0.19782 | 2.515 | 0.0007812 | 2.5452 | 0.882 | 0.0006552 | 0 | XLPE 1200mm2 | 12.6 | [6 empty] | 444 | 426 | 0 | 0 | B_CEST_HELI | HLIOPLIS | CAIROEST |  | محول تيار |  |  | 0.00040872 | 0.0051962 | 0.3781 | 0.0052587 | 0.0018223 | 0.31712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صقر قريس | جاردينيا | SKR-KORSH | GARDENIA | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 1.89 | 1200/1 | 2000/1 | 1100 | 419.144 | 1200 | 4.725e-05 | 0.00047445 | 0.040249 | 0.00080208 | 0.00027881 | 0.048482 | 0 | 0.022869 | 0.22963 | 8.316e-05 | 0.38821 | 0.13495 | 0.00010017 | 0 | XLPE 1600mm2 Elswedy | 1.89 | [6 empty] | 428 | 431 | 0 | 0 | B_SKR_GRD_1 | SKRKRISH | GARDENIA |  |  |  |  | 4.725e-05 | 0.00047445 | 0.040249 | 0.00080208 | 0.00027881 | 0.048482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صقر قريس | جاردينيا | SKR-KORSH | GARDENIA | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 1.89 | 1200/1 | 2000/1 | 1100 | 419.144 | 1200 | 4.725e-05 | 0.00047445 | 0.040249 | 0.00080208 | 0.00027881 | 0.048482 | 0 | 0.022869 | 0.22963 | 8.316e-05 | 0.38821 | 0.13495 | 0.00010017 | 0 | XLPE 1600mm2 Elswedy | 1.89 | [6 empty] | 428 | 431 | 0 | 0 | B_SKR_GRD_2 | SKRKRISH | GARDENIA |  |  |  |  | 4.725e-05 | 0.00047445 | 0.040249 | 0.00080208 | 0.00027881 | 0.048482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | جاردينيا | CAIRO-EST | GARDENIA | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 6.5 | 800/1 | 2000/1 | 800 | 304.832 | 1200 | 0.0001625 | 0.0016317 | 0.13842 | 0.0027585 | 0.00095888 | 0.16674 | 0 | 0.07865 | 0.78975 | 0.000286 | 1.3351 | 0.4641 | 0.0003445 | 0 | XLPE 1600mm2 Elswedy | 6.5 | [6 empty] | 426 | 431 | 0 | 0 | B_CEST_GRD_1 | CAIROEST | GARDENIA |  | محول تيار |  |  | 0.0001625 | 0.0016317 | 0.13842 | 0.0027585 | 0.00095888 | 0.16674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | جاردينيا | CAIRO-EST | GARDENIA | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 6.5 | 800/1 | 2000/1 | 800 | 304.832 | 1200 | 0.0001625 | 0.0016317 | 0.13842 | 0.0027585 | 0.00095888 | 0.16674 | 0 | 0.07865 | 0.78975 | 0.000286 | 1.3351 | 0.4641 | 0.0003445 | 0 | XLPE 1600mm2 Elswedy | 6.5 | [6 empty] | 426 | 431 | 0 | 0 | B_CEST_GRD_2 | CAIROEST | GARDENIA |  | محول تيار |  |  | 0.0001625 | 0.0016317 | 0.13842 | 0.0027585 | 0.00095888 | 0.16674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | صقر قريش | CAIRO-EST | SKR-KORSH | القاهرة | Cable | 3 | 220 | XLPE 1200mm2 | 10.5 | 800/1 | 1200/1 | 800 | 304.832 | 950 | 0.0003406 | 0.0043302 | 0.31508 | 0.0043822 | 0.0015186 | 0.26426 | 0 | 0.16485 | 2.0958 | 0.000651 | 2.121 | 0.735 | 0.000546 | 0 | XLPE 1200mm2 | 10.5 | [6 empty] | 426 | 428 | 0 | 0 | B_CEST_SKR_3 | CAIROEST | SKRKRISH |  | محول تيار |  |  | 0.0003406 | 0.0043302 | 0.31508 | 0.0043822 | 0.0015186 | 0.26426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2 | المستقبل | S2 | MOSTKBL | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy energy | 7.068 | 2500/1 | 2500/1 | 1170 | 445.8168 | 1400 | 0.00018794 | 0.0024585 | 0.24716 | 0.0022451 | 0.00093023 | 0.20525 | 0 | 0.090965 | 1.1899 | 0.00051066 | 1.0866 | 0.45023 | 0.00042408 | 0 | XLPE 2000mm2 Elswedy energy | 7.068 | [6 empty] | 449 | 483 | 0 | 0 |  | S2_CPTAL | M_CITY |  |  |  |  | 0.00018794 | 0.0024585 | 0.24716 | 0.0022451 | 0.00093023 | 0.20525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2 | المستقبل | S2 | MOSTKBL | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy energy | 7.068 | 2500/1 | 2500/1 | 1170 | 445.8168 | 1400 | 0.00018794 | 0.0024585 | 0.24716 | 0.0022451 | 0.00093023 | 0.20525 | 0 | 0.090965 | 1.1899 | 0.00051066 | 1.0866 | 0.45023 | 0.00042408 | 0 | XLPE 2000mm2 Elswedy energy | 7.068 | [6 empty] | 449 | 483 | 0 | 0 |  | S2_CPTAL | M_CITY |  |  |  |  | 0.00018794 | 0.0024585 | 0.24716 | 0.0022451 | 0.00093023 | 0.20525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البساتين | المستثمرين | BASATEEN | MOSTSMRN | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy energy | 8.33 | 1200/1 | 2500/1 | 1170 | 445.8168 | 1400 | 0.0002215 | 0.0028974 | 0.29129 | 0.002646 | 0.0010963 | 0.2419 | 0 | 0.10721 | 1.4024 | 0.00060184 | 1.2807 | 0.53062 | 0.0004998 | 0 | XLPE 2000mm2 Elswedy energy | 8.33 | [6 empty] | 424 | 425 | 0 | 0 | B_BSTN_MSTS_1 | BASATEEN | MSTSMREN |  | محول تيار |  |  | 0.0002215 | 0.0028974 | 0.29129 | 0.002646 | 0.0010963 | 0.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البساتين | المستثمرين | BASATEEN | MOSTSMRN | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy energy | 8.33 | 1200/1 | 2500/1 | 1170 | 445.8168 | 1400 | 0.0002215 | 0.0028974 | 0.29129 | 0.002646 | 0.0010963 | 0.2419 | 0 | 0.10721 | 1.4024 | 0.00060184 | 1.2807 | 0.53062 | 0.0004998 | 0 | XLPE 2000mm2 Elswedy energy | 8.33 | [6 empty] | 424 | 425 | 0 | 0 | B_BSTN_MSTS_2 | BASATEEN | MSTSMREN |  | محول تيار |  |  | 0.0002215 | 0.0028974 | 0.29129 | 0.002646 | 0.0010963 | 0.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المستثمرين | الشرق | MOSTSMRN | CAIRO-EST | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 8.17 | 2500/1 | 800/1 | 800 | 304.832 | 1400 | 0.00021725 | 0.0028418 | 0.28321 | 0.0025952 | 0.0017721 | 0.23726 | 0 | 0.10515 | 1.3754 | 0.00058514 | 1.2561 | 0.85769 | 0.0004902 | 0 | XLPE 2000mm2 Elswedy | 8.17 | [6 empty] | 425 | 426 | 0 | 0 | B_CEST_MSTS_1 | MSTSMREN | CAIROEST |  | محول تيار |  |  | 0.00021725 | 0.0028418 | 0.28321 | 0.0025952 | 0.0017721 | 0.23726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرق | المقطم | CAIRO-EST | MOKATTAM | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 2000mm2 Elswedy | 6.1 | 800/1 | 1600/1 | 800 | 304.832 | 1200 | 0.00026171 | 0.0025912 | 0.15558 | 0.001784 | 0.0042911 | 0.12961 | 0.0020723 | 0.12667 | 1.2541 | 0.00032145 | 0.86346 | 2.0769 | 0.00026779 | 1.003 | 2*380/50 ACSR | 1.7 | XLPE 2000mm2 Elswedy | 4.4 |  |  |  |  | 426 | 455 | 0 | 0 | B_CEST_MOKATM | CAIROEST | Z_MOKATM |  | محول تيار |  |  | 0.00014471 | 0.0010607 | 0.0030608 | 0.00038636 | 0.0033368 | 0.0018348 | 0.0020723 | 0.000117 | 0.0015305 | 0.15252 | 0.0013976 | 0.00095436 | 0.12778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المستثمرين | المقطم | MOSTSMRN | MOKATTAM | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 2000mm2 Elswedy Thermal Invar 1*238/97 | 5.87 | 2500/1 | 1600/1 | 1170 | 445.8168 | 1200 | 0.00033931 | 0.0027374 | 0.13425 | 0.001864 | 0.0052145 | 0.11165 | 0.0027135 | 0.16423 | 1.3249 | 0.00027737 | 0.90219 | 2.5238 | 0.00023069 | 1.3133 | 2*380/50 ACSR | 1.7 | XLPE 2000mm2 Elswedy | 3.77 | Thermal Invar 1*238/97 | 0.4 |  |  | 425 | 455 | 0 | 0 | B_MSTSM_MOKATM | MSTSMREN | Z_MOKATM |  |  |  |  | 0.00014471 | 0.0010607 | 0.0030608 | 0.00038636 | 0.0033368 | 0.0018348 | 0.0020723 | 0.00010025 | 0.0013113 | 0.13068 | 0.0011975 | 0.00081772 | 0.10948 | 0 | 9.4353e-05 | 0.00036532 | 0.00050246 | 0.00028014 | 0.00106 | 0.00033711 | 0.00064114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العبورالجديدة | النهضة | OBOUR | NAHDA | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 5.5 | 1600/1 | 2500/1 | 1200 | 457.248 | 1400 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0.070785 | 0.92592 | 0.00039391 | 0.84557 | 0.57739 | 0.00033 | 0 | XLPE 2000mm2 Elswedy | 5.5 | [6 empty] | 443 | 457 | 0 | 0 | B_OBOR_NHDA_1 | AL_OBOUR | NAHDA |  |  |  |  | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العبورالجديدة | النهضة | OBOUR | NAHDA | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 5.5 | 1600/1 | 2500/1 | 1200 | 457.248 | 1400 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0.070785 | 0.92592 | 0.00039391 | 0.84557 | 0.57739 | 0.00033 | 0 | XLPE 2000mm2 Elswedy | 5.5 | [6 empty] | 443 | 457 | 0 | 0 | B_OBOR_NHDA_2 | AL_OBOUR | NAHDA |  |  |  |  | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
هليوبوليس | النهضة | HELUPLS | NAHDA | القاهرة | Circuit & Cable | 1 | 220 | 1*506 AAAC XLPE 1600mm2 Elswedy 2*380/50 ACSR XLPE 2000mm2 Elswedy | 29 | 1600/1 | 2500/1 | 900 | 342.936 | 900 | 0.0021427 | 0.014525 | 0.42453 | 0.011807 | 0.029166 | 0.43081 | 0.016457 | 1.0371 | 7.0299 | 0.00087713 | 5.7146 | 14.1164 | 0.0008901 | 7.965 | 1*506 AAAC | 7 | XLPE 1600mm2 Elswedy | 10 | 2*380/50 ACSR | 6.5 | XLPE 2000mm2 Elswedy | 5.5 | 444 | 457 | 0 | 0 | B_HELI_NHDA_1 | HLIOPLIS | NAHDA |  |  |  |  | 0.0011932 | 0.0060455 | 0.0092154 | 0.0043388 | 0.01374 | 0.0075552 | 0.0085331 | 0.00025 | 0.0025103 | 0.21296 | 0.0042438 | 0.0014752 | 0.25652 | 0 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0
هليوبوليس | النهضة | HELUPLS | NAHDA | القاهرة | Circuit & Cable | 2 | 220 | 1*506 AAAC Two Cable in Parralel of Cable L-Pr Brilli800 2*380/50 ACSR XLPE 2000mm2 Elswedy | 28.5 | 1600/1 | 2500/1 | 900 | 342.936 | 900 | 0.0021096 | 0.01383 | 1.0208 | 0.0099872 | 0.03672 | 0.77019 | 0.016457 | 1.0211 | 6.6937 | 0.0021091 | 4.8338 | 17.7724 | 0.0015913 | 7.965 | 1*506 AAAC | 7 | Two Cable in Parralel of Cable L-Pr Brilli800 | 9.5 | 2*380/50 ACSR | 6.5 | XLPE 2000mm2 Elswedy | 5.5 | 444 | 457 | 0 | 0 | B_HELI_NHDA_2 | HLIOPLIS | NAHDA |  |  |  |  | 0.0011932 | 0.0060455 | 0.0092154 | 0.0043388 | 0.01374 | 0.0075552 | 0.0085331 | 0.00021689 | 0.0018156 | 0.80925 | 0.0024241 | 0.0090289 | 0.5959 | 0 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0
ابوزعبل | العبورالجديدة | ABO-ZABAL | OBOUR | القاهرة | Circuit | 1 | 220 | Thermal 1*290/88 2*380/50 ACSR | 7.5 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00086457 | 0.0051138 | 0.012687 | 0.0024142 | 0.015752 | 0.0077401 | 0.0097183 | 0.41845 | 2.4751 | 2.6213e-05 | 1.1685 | 7.6239 | 1.5992e-05 | 4.7037 | Thermal 1*290/88 | 1.5 | 2*380/50 ACSR | 6 |  |  |  |  | 442 | 443 | 0 | 0 | B_AZAB_OBOR_1 | ABUZABAL | AL_OBOUR |  | تم التواصل مع م عمرو امية من خطوط القاهرة تليفون 01115288547 يوم 3 ابريل 2023 وافاد انه يوجد مشروع مستقبلي بجعل الخط حراري مزدوج |  |  | 0.00035382 | 0.00137 | 0.0018842 | 0.0010505 | 0.003975 | 0.0012642 | 0.0024043 | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوزعبل | العبورالجديدة | ABO-ZABAL | OBOUR | القاهرة | Circuit | 2 | 220 | Thermal 1*290/88 2*380/50 ACSR | 7.5 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00086457 | 0.0051138 | 0.012687 | 0.0024142 | 0.015752 | 0.0077401 | 0.0097183 | 0.41845 | 2.4751 | 2.6213e-05 | 1.1685 | 7.6239 | 1.5992e-05 | 4.7037 | Thermal 1*290/88 | 1.5 | 2*380/50 ACSR | 6 |  |  |  |  | 442 | 443 | 0 | 0 | B_AZAB_OBOR_2 | ABUZABAL | AL_OBOUR |  | تم التواصل مع م عمرو امية من خطوط القاهرة تليفون 01115288547 يوم 3 ابريل 2023 وافاد انه يوجد مشروع مستقبلي بجعل الخط حراري مزدوج |  |  | 0.00035382 | 0.00137 | 0.0018842 | 0.0010505 | 0.003975 | 0.0012642 | 0.0024043 | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المطار | القاهرة الجديدة | MATAR | NEWCAIRO | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1200mm2 XLPE 2000mm2 Elswedy | 8.4 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00057134 | 0.0045985 | 0.094503 | 0.0022343 | 0.011967 | 0.076688 | 0.0071312 | 0.27653 | 2.2257 | 0.00019525 | 1.0814 | 5.792 | 0.00015845 | 3.4515 | 2*380/50 ACSR | 5.85 | XLPE 1200mm2 | 0.95 | XLPE 2000mm2 Elswedy | 1.6 |  |  | 429 | 430 | 0 | 0 | B_CGAD_MATAR_1 | MATTAR | CGADIDA |  |  |  |  | 0.00049798 | 0.0036502 | 0.010533 | 0.0013295 | 0.011482 | 0.006314 | 0.0071312 | 3.0816e-05 | 0.00039178 | 0.028508 | 0.00039649 | 0.0001374 | 0.02391 | 0 | 4.2545e-05 | 0.00055653 | 0.055463 | 0.00050823 | 0.00034704 | 0.046464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المطار | القاهرة الجديدة | MATAR | NEWCAIRO | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1200mm2 XLPE 2000mm2 Elswedy | 8.4 | 1600/1 | 1600/1 | 900 | 342.936 | 950 | 0.00057134 | 0.0045985 | 0.094503 | 0.0022343 | 0.011967 | 0.076688 | 0.0071312 | 0.27653 | 2.2257 | 0.00019525 | 1.0814 | 5.792 | 0.00015845 | 3.4515 | 2*380/50 ACSR | 5.85 | XLPE 1200mm2 | 0.95 | XLPE 2000mm2 Elswedy | 1.6 |  |  | 429 | 430 | 0 | 0 | B_CGAD_MATAR_2 | MATTAR | CGADIDA |  |  |  |  | 0.00049798 | 0.0036502 | 0.010533 | 0.0013295 | 0.011482 | 0.006314 | 0.0071312 | 3.0816e-05 | 0.00039178 | 0.028508 | 0.00039649 | 0.0001374 | 0.02391 | 0 | 4.2545e-05 | 0.00055653 | 0.055463 | 0.00050823 | 0.00034704 | 0.046464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صقر قريس | المطار | SKR-KORSH | MATAR | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 2.3 | 1200/1 | 1600/1 | 1170 | 445.8168 | 1295 | 6.1159e-05 | 0.00080001 | 0.079727 | 0.00073058 | 0.00049887 | 0.066792 | 0 | 0.029601 | 0.3872 | 0.00016473 | 0.3536 | 0.24145 | 0.000138 | 0 | XLPE 2000mm2 Elswedy | 2.3 | [6 empty] | 428 | 429 | 0 | 0 | B_SAKR_MATAR_1 | SKRKRISH | MATTAR |  |  |  |  | 6.1159e-05 | 0.00080001 | 0.079727 | 0.00073058 | 0.00049887 | 0.066792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صقر قريس | المطار | SKR-KORSH | MATAR | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 2.3 | 1200/1 | 1600/1 | 1170 | 445.8168 | 1295 | 6.1159e-05 | 0.00080001 | 0.079727 | 0.00073058 | 0.00049887 | 0.066792 | 0 | 0.029601 | 0.3872 | 0.00016473 | 0.3536 | 0.24145 | 0.000138 | 0 | XLPE 2000mm2 Elswedy | 2.3 | [6 empty] | 428 | 429 | 0 | 0 | B_SAKR_MATAR_2 | SKRKRISH | MATTAR |  |  |  |  | 6.1159e-05 | 0.00080001 | 0.079727 | 0.00073058 | 0.00049887 | 0.066792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد التبين | جنوب التبين | TEBB-GEN | SOTH.TEBBEN | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 | 7.8 | 1600/1 | 1600/1 | 950 | 361.988 | 950 | 0.00025302 | 0.0032167 | 0.23406 | 0.0032554 | 0.0011281 | 0.19631 | 0 | 0.12246 | 1.5569 | 0.0004836 | 1.5756 | 0.546 | 0.0004056 | 0 | XLPE 1200mm2 | 7.8 | [6 empty] | 434 | 436 | 0 | 0 | B_NTEB_TBTH_1 | TEBBINTH | N_TEBBIN |  |  |  |  | 0.00025302 | 0.0032167 | 0.23406 | 0.0032554 | 0.0011281 | 0.19631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد التبين | جنوب التبين | TEBB-GEN | SOTH.TEBBEN | القاهرة | Cable | 2 | 220 | XLPE 1200mm2 | 7.8 | 1600/1 | 1600/1 | 950 | 361.988 | 950 | 0.00025302 | 0.0032167 | 0.23406 | 0.0032554 | 0.0011281 | 0.19631 | 0 | 0.12246 | 1.5569 | 0.0004836 | 1.5756 | 0.546 | 0.0004056 | 0 | XLPE 1200mm2 | 7.8 | [6 empty] | 434 | 436 | 0 | 0 | B_NTEB_TBTH_2 | TEBBINTH | N_TEBBIN |  |  |  |  | 0.00025302 | 0.0032167 | 0.23406 | 0.0032554 | 0.0011281 | 0.19631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي حوف | توليد التبين | WADI-HOF | TEBB-GEN | القاهرة | Circuit & Cable | 1 | 220 | XLPE 1200mm2 Thermal 1*439/46 GT A.C.S.R 2*380/50 ACSR | 35.36 | 1600/1 | 1600/1 | 700 | 266.728 | 950 | 0.0066748 | 0.028246 | 0.26617 | 0.022273 | 0.073959 | 0.21726 | 0.044081 | 3.2306 | 13.6713 | 0.00054993 | 10.7802 | 35.7962 | 0.00044889 | 21.3353 | XLPE 1200mm2 | 7.7 | Thermal 1*439/46 GT A.C.S.R | 27 | 2*380/50 ACSR | 0.66 |  |  | 432 | 434 | 0 | 0 | B_TBTH_WHOF_1 | WADIHOF | TEBBINTH |  |  |  |  | 0.00024977 | 0.0031755 | 0.23106 | 0.0032136 | 0.0011136 | 0.19379 | 0 | 0.0063688 | 0.024659 | 0.033916 | 0.01891 | 0.07155 | 0.022755 | 0.043277 | 5.6182e-05 | 0.00041182 | 0.0011883 | 0.00015 | 0.0012955 | 0.00071235 | 0.00080455 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي حوف | توليد التبين | WADI-HOF | TEBB-GEN | القاهرة | Circuit & Cable | 2 | 220 | XLPE 1200mm2 Thermal 1*439/46 GT A.C.S.R 2*380/50 ACSR | 35.36 | 1600/1 | 1600/1 | 700 | 266.728 | 950 | 0.0066748 | 0.028246 | 0.26617 | 0.022273 | 0.073959 | 0.21726 | 0.044081 | 3.2306 | 13.6713 | 0.00054993 | 10.7802 | 35.7962 | 0.00044889 | 21.3353 | XLPE 1200mm2 | 7.7 | Thermal 1*439/46 GT A.C.S.R | 27 | 2*380/50 ACSR | 0.66 |  |  | 432 | 434 | 0 | 0 | B_TBTH_WHOF_2 | WADIHOF | TEBBINTH |  |  |  |  | 0.00024977 | 0.0031755 | 0.23106 | 0.0032136 | 0.0011136 | 0.19379 | 0 | 0.0063688 | 0.024659 | 0.033916 | 0.01891 | 0.07155 | 0.022755 | 0.043277 | 5.6182e-05 | 0.00041182 | 0.0011883 | 0.00015 | 0.0012955 | 0.00071235 | 0.00080455 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محولات الشمال | بهتيم 2 | CAIRO.NRTH | BAHTEM-II | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 3.835 | 1500/1 | 1600/1 | 1200 | 457.248 | 1300 | 0.00010198 | 0.0013339 | 0.13294 | 0.0012182 | 0.00083181 | 0.11137 | 0 | 0.049356 | 0.64562 | 0.00027466 | 0.58959 | 0.4026 | 0.0002301 | 0 | XLPE 2000mm2 Elswedy | 3.835 | [6 empty] | 450 | 474 | 0 | 0 | B_CNTH_NBHT_1 | CAIRONTH | NBAHTEEM |  |  |  |  | 0.00010198 | 0.0013339 | 0.13294 | 0.0012182 | 0.00083181 | 0.11137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محولات الشمال | بهتيم 2 | CAIRO.NRTH | BAHTEM-II | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 3.835 | 1500/1 | 1600/1 | 1200 | 457.248 | 1300 | 0.00010198 | 0.0013339 | 0.13294 | 0.0012182 | 0.00083181 | 0.11137 | 0 | 0.049356 | 0.64562 | 0.00027466 | 0.58959 | 0.4026 | 0.0002301 | 0 | XLPE 2000mm2 Elswedy | 3.835 | [6 empty] | 450 | 474 | 0 | 0 | B_CNTH_NBHT_2 | CAIRONTH | NBAHTEEM |  |  |  |  | 0.00010198 | 0.0013339 | 0.13294 | 0.0012182 | 0.00083181 | 0.11137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بهتيم 2 | بهتيم | BAHTEM-II | BAHTEM-I | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 | 0.135 | 1600/1 | 1200/1 | 950 | 361.988 | 950 | 4.3791e-06 | 5.5674e-05 | 0.0040511 | 5.6343e-05 | 1.9525e-05 | 0.0033977 | 0 | 0.0021195 | 0.026946 | 8.37e-06 | 0.02727 | 0.00945 | 7.02e-06 | 0 | XLPE 1200mm2 | 0.135 | [6 empty] | 474 | 476 | 0 | 0 | B_BHTM_NBHT_1 | NBAHTEEM | BAHTEEM |  |  |  |  | 4.3791e-06 | 5.5674e-05 | 0.0040511 | 5.6343e-05 | 1.9525e-05 | 0.0033977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بهتيم 2 | بهتيم | BAHTEM-II | BAHTEM-I | القاهرة | Cable | 2 | 220 | XLPE 1200mm2 | 0.135 | 1600/1 | 1200/1 | 950 | 361.988 | 950 | 4.3791e-06 | 5.5674e-05 | 0.0040511 | 5.6343e-05 | 1.9525e-05 | 0.0033977 | 0 | 0.0021195 | 0.026946 | 8.37e-06 | 0.02727 | 0.00945 | 7.02e-06 | 0 | XLPE 1200mm2 | 0.135 | [6 empty] | 474 | 476 | 0 | 0 | B_BHTM_NBHT_2 | NBAHTEEM | BAHTEEM |  |  |  |  | 4.3791e-06 | 5.5674e-05 | 0.0040511 | 5.6343e-05 | 1.9525e-05 | 0.0033977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشيخ زايد | توليد اكتوبر | ZAID | OCT-GEN | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 13 | 1600/1 | 2000/1 | 1100 | 419.144 | 1200 | 0.000325 | 0.0032634 | 0.27685 | 0.0055169 | 0.0019178 | 0.33348 | 0 | 0.1573 | 1.5795 | 0.000572 | 2.6702 | 0.9282 | 0.000689 | 0 | XLPE 1600mm2 Elswedy | 13 | [6 empty] | 414 | 415 | 0 | 0 | B_OCTG_ZAYD_1 | ZAYD | 6_OCTG |  | خطاب رسمي من مقيم مشروع توسعات محطة اكتوبر افاد ان سعة التحميل 1092 امبير |  |  | 0.000325 | 0.0032634 | 0.27685 | 0.0055169 | 0.0019178 | 0.33348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشيخ زايد | توليد اكتوبر | ZAID | OCT-GEN | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 13 | 1600/1 | 2000/1 | 1100 | 419.144 | 1200 | 0.000325 | 0.0032634 | 0.27685 | 0.0055169 | 0.0019178 | 0.33348 | 0 | 0.1573 | 1.5795 | 0.000572 | 2.6702 | 0.9282 | 0.000689 | 0 | XLPE 1600mm2 Elswedy | 13 | [6 empty] | 414 | 415 | 0 | 0 | B_OCTG_ZAYD_2 | ZAYD | 6_OCTG |  | خطاب رسمي من مقيم مشروع توسعات محطة اكتوبر افاد ان سعة التحميل 1092 امبير |  |  | 0.000325 | 0.0032634 | 0.27685 | 0.0055169 | 0.0019178 | 0.33348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
التبين 500 | 15 مايو | TEBB.500 | 15MAYO | القاهرة | Circuit | 1 | 220 | 1*380/88 ACSR Thermal Invar 1*255/88 | 12.674 | 2000/1 | 1600/1 | 650 | 247.676 | 650 | 0.0021887 | 0.010477 | 0.017478 | 0.0078585 | 0.0249 | 0.013671 | 0.015463 | 1.0593 | 5.071 | 3.6112e-05 | 3.8035 | 12.0516 | 2.8246e-05 | 7.484 | 1*380/88 ACSR | 12.64 | Thermal Invar 1*255/88 | 0.034 |  |  |  |  | 438 | 451 | 0 | 0 | B_TEP50_15MY_1 | TBNPS500 | 15_MAY |  | تم الاتصال ب م عمرو امية من خطوط القاهرة تليفون 01115288547 يوم 13 فبراير 2022 وافاد بوجود الموصل 1*380 كما هو |  |  | 0.0021807 | 0.010446 | 0.017436 | 0.0078347 | 0.02481 | 0.013643 | 0.015408 | 8.02e-06 | 3.1052e-05 | 4.2709e-05 | 2.3812e-05 | 9.01e-05 | 2.8655e-05 | 5.4497e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
التبين 500 | 15 مايو | TEBB.500 | 15MAYO | القاهرة | Circuit | 2 | 220 | Thermal Invar 1*255/88 | 12.674 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0029896 | 0.011575 | 0.01592 | 0.0088763 | 0.033586 | 0.010681 | 0.020314 | 1.447 | 5.6024 | 3.2893e-05 | 4.2961 | 16.2557 | 2.2069e-05 | 9.8322 | Thermal Invar 1*255/88 | 12.674 | [6 empty] | 438 | 451 | 0 | 0 | B_TEP50_15MY_2 | TBNPS500 | 15_MAY |  |  |  |  | 0.0029896 | 0.011575 | 0.01592 | 0.0088763 | 0.033586 | 0.010681 | 0.020314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الرخام والجرانيت | 15 مايو | ROKHM&GRNET | 15MAYO | القاهرة | Circuit | 1 | 220 | 1*380/88 ACSR 2*405 AAAC Thermal Invar 1*255/88 | 89.774 | 2000/1 | 1600/1 | 650 | 247.676 | 650 | 0.015198 | 0.073381 | 0.12464 | 0.054173 | 0.17519 | 0.096887 | 0.10945 | 7.3561 | 35.5162 | 0.00025753 | 26.2195 | 84.7926 | 0.00020018 | 52.973 | 1*380/88 ACSR | 85.54 | 2*405 AAAC | 4.2 | Thermal Invar 1*255/88 | 0.034 |  |  | 311 | 451 | 0 | 0 | B_ROKHM_15MY_1 | ROKHAM_G | 15_MAY |  | تم الاتصال ب م عمرو امية من خطوط القاهرة تليفون 01115288547 يوم 13 فبراير 2022 وافاد بوجود الموصل 1*380 كما هو |  |  | 0.014757 | 0.070694 | 0.11799 | 0.053021 | 0.1679 | 0.092325 | 0.10427 | 0.00043302 | 0.0026554 | 0.0066066 | 0.0011281 | 0.0072025 | 0.0045331 | 0.0051198 | 8.02e-06 | 3.1052e-05 | 4.2709e-05 | 2.3812e-05 | 9.01e-05 | 2.8655e-05 | 5.4497e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الرخام والجرانيت | 15 مايو | ROKHM&GRNET | 15MAYO | القاهرة | Circuit | 2 | 220 | 1*380/88 ACSR 2*405 AAAC Thermal Invar 1*255/88 | 89.774 | 2000/1 | 1600/1 | 650 | 247.676 | 650 | 0.016466 | 0.075118 | 0.12218 | 0.055783 | 0.18894 | 0.092156 | 0.11712 | 7.9694 | 36.357 | 0.00025243 | 26.9989 | 91.4446 | 0.00019041 | 56.6885 | 1*380/88 ACSR | 65.54 | 2*405 AAAC | 4.2 | Thermal Invar 1*255/88 | 20.034 |  |  | 311 | 451 | 0 | 0 | B_ROKHM_15MY_2 | ROKHAM_G | 15_MAY |  | تم الاتصال ب م عمرو امية من خطوط القاهرة تليفون 01115288547 يوم 13 فبراير 2022 وافاد بوجود الموصل 1*380 كما هو |  |  | 0.011307 | 0.054165 | 0.090406 | 0.040624 | 0.12864 | 0.070739 | 0.079894 | 0.00043302 | 0.0026554 | 0.0066066 | 0.0011281 | 0.0072025 | 0.0045331 | 0.0051198 | 0.0047257 | 0.018297 | 0.025166 | 0.014031 | 0.05309 | 0.016884 | 0.032111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | توسيع توليد اكتوبر | HADABA-I | OCT-EX-GEN | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 12.5 | 2000/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0003125 | 0.0031379 | 0.2662 | 0.0053048 | 0.001844 | 0.32065 | 0 | 0.15125 | 1.5188 | 0.00055 | 2.5675 | 0.8925 | 0.0006625 | 0 | XLPE 1600mm2 Elswedy | 12.5 | [6 empty] | 408 | 417 | 0 | 0 | B_HDBA_OCTG2_1 | 6_OCTG_2 | HADABA |  | يوجد كابل 1600 mm بين القضبان والخط افادت محطة توليد اكتوبر 2 انه يتحمل 1092 امبير |  |  | 0.0003125 | 0.0031379 | 0.2662 | 0.0053048 | 0.001844 | 0.32065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | توسيع توليد اكتوبر | HADABA-I | OCT-EX-GEN | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 12.5 | 2000/1 | 1600/1 | 1100 | 419.144 | 1200 | 0.0003125 | 0.0031379 | 0.2662 | 0.0053048 | 0.001844 | 0.32065 | 0 | 0.15125 | 1.5188 | 0.00055 | 2.5675 | 0.8925 | 0.0006625 | 0 | XLPE 1600mm2 Elswedy | 12.5 | [6 empty] | 408 | 417 | 0 | 0 | B_HDBA_OCTG2_2 | 6_OCTG_2 | HADABA |  | يوجد كابل 1600 mm بين القضبان والخط افادت محطة توليد اكتوبر 2 انه يتحمل 1092 امبير |  |  | 0.0003125 | 0.0031379 | 0.2662 | 0.0053048 | 0.001844 | 0.32065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد اكتوبر | توسيع توليد اكتوبر | OCT-GEN | OCT-EX-GEN | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 0.28 | 2000/1 | 2000/1 | 1100 | 419.144 | 1200 | 7e-06 | 7.0289e-05 | 0.0059629 | 0.00011883 | 4.1306e-05 | 0.0071826 | 0 | 0.003388 | 0.03402 | 1.232e-05 | 0.057512 | 0.019992 | 1.484e-05 | 0 | XLPE 1600mm2 Elswedy | 0.28 | [6 empty] | 415 | 417 | 0 | 0 | B_OCTG2_OCTG1 | 6_OCTG | 6_OCTG_2 |  | يوجد كابل 1600 mm بين القضبان والخط افادت محطة توليد اكتوبر 2 انه يتحمل 1092 امبير |  |  | 7e-06 | 7.0289e-05 | 0.0059629 | 0.00011883 | 4.1306e-05 | 0.0071826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المستثمرين | القطامية | MOSTSMRN | KATAMIA | القاهرة | Circuit & Cable | 1 | 220 | XLPE 1600mm2 Elswedy 2*380/50 ACSR XLPE 2000mm2 Elswedy | 26.916 | 2500/1 | 2500/1 | 1050 | 400.092 | 1200 | 0.001907 | 0.014499 | 0.18691 | 0.0072752 | 0.041253 | 0.1901 | 0.02499 | 0.923 | 7.0174 | 0.00038618 | 3.5212 | 19.9667 | 0.00039276 | 12.095 | XLPE 1600mm2 Elswedy | 5.416 | 2*380/50 ACSR | 20.5 | XLPE 2000mm2 Elswedy | 1 |  |  | 425 | 440 | 0 | 0 |  | MSTSMREN | KATAMIA |  |  |  |  | 0.0001354 | 0.0013596 | 0.11534 | 0.0022984 | 0.00079897 | 0.13893 | 0 | 0.001745 | 0.012791 | 0.03691 | 0.0046591 | 0.040238 | 0.022126 | 0.02499 | 2.6591e-05 | 0.00034783 | 0.034664 | 0.00031764 | 0.0002169 | 0.02904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المستثمرين | القطامية | MOSTSMRN | KATAMIA | القاهرة | Circuit & Cable | 2 | 220 | XLPE 1600mm2 Elswedy 2*380/50 ACSR XLPE 2000mm2 Elswedy | 26.916 | 2500/1 | 2500/1 | 1050 | 400.092 | 1200 | 0.001907 | 0.014499 | 0.18691 | 0.0072752 | 0.041253 | 0.1901 | 0.02499 | 0.923 | 7.0174 | 0.00038618 | 3.5212 | 19.9667 | 0.00039276 | 12.095 | XLPE 1600mm2 Elswedy | 5.416 | 2*380/50 ACSR | 20.5 | XLPE 2000mm2 Elswedy | 1 |  |  | 425 | 440 | 0 | 0 |  | MSTSMREN | KATAMIA |  |  |  |  | 0.0001354 | 0.0013596 | 0.11534 | 0.0022984 | 0.00079897 | 0.13893 | 0 | 0.001745 | 0.012791 | 0.03691 | 0.0046591 | 0.040238 | 0.022126 | 0.02499 | 2.6591e-05 | 0.00034783 | 0.034664 | 0.00031764 | 0.0002169 | 0.02904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوطنية | زهراء المعادي | WATANIA | ZHRA.MAADI | القاهرة | Circuit & Cable | 1 | 220 | 3*380/50 ACSR XLPE 2500mm2 | 9.655 | 2000/1 | 2000/1 | 1800 | 685.872 | 1800 | 0.0004306 | 0.0058521 | 0.022599 | 0.0049032 | 0.015385 | 0.017099 | 0.0045287 | 0.20841 | 2.8324 | 4.6691e-05 | 2.3731 | 7.4465 | 3.5328e-05 | 2.1919 | 3*380/50 ACSR | 9.53 | XLPE 2500mm2 | 0.125 |  |  |  |  | 437 | 439 | 0 | 0 | B_WATN_MAADI_1 | WATANIA | ZAHRAA_M |  |  |  |  | 0.00042727 | 0.0058086 | 0.018266 | 0.0048635 | 0.015358 | 0.013469 | 0.0045287 | 3.3239e-06 | 4.3479e-05 | 0.004333 | 3.9706e-05 | 2.7113e-05 | 0.00363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوطنية | زهراء المعادي | WATANIA | ZHRA.MAADI | القاهرة | Circuit & Cable | 2 | 220 | 3*380/50 ACSR XLPE 2500mm2 | 9.655 | 2000/1 | 2000/1 | 1800 | 685.872 | 1800 | 0.0004306 | 0.0058521 | 0.022599 | 0.0049032 | 0.015385 | 0.017099 | 0.0045287 | 0.20841 | 2.8324 | 4.6691e-05 | 2.3731 | 7.4465 | 3.5328e-05 | 2.1919 | 3*380/50 ACSR | 9.53 | XLPE 2500mm2 | 0.125 |  |  |  |  | 437 | 439 | 0 | 0 | B_WATN_MAADI_2 | WATANIA | ZAHRAA_M |  |  |  |  | 0.00042727 | 0.0058086 | 0.018266 | 0.0048635 | 0.015358 | 0.013469 | 0.0045287 | 3.3239e-06 | 4.3479e-05 | 0.004333 | 3.9706e-05 | 2.7113e-05 | 0.00363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بيانكو | التبين 500 | BIANCO | TEBB.500 | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 1.8 | 1600/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00015322 | 0.0011231 | 0.0032409 | 0.00040909 | 0.0035331 | 0.0019428 | 0.0021942 | 0.07416 | 0.5436 | 6.696e-06 | 0.198 | 1.71 | 4.014e-06 | 1.062 | 2*380/50 ACSR | 1.8 | [6 empty] | 433 | 438 | 0 | 0 |  |  | TBNPS500 |  |  |  |  | 0.00015322 | 0.0011231 | 0.0032409 | 0.00040909 | 0.0035331 | 0.0019428 | 0.0021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بيانكو | التبين 500 | BIANCO | TEBB.500 | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR | 1.8 | 1600/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.00015322 | 0.0011231 | 0.0032409 | 0.00040909 | 0.0035331 | 0.0019428 | 0.0021942 | 0.07416 | 0.5436 | 6.696e-06 | 0.198 | 1.71 | 4.014e-06 | 1.062 | 2*380/50 ACSR | 1.8 | [6 empty] | 433 | 438 | 0 | 0 |  |  | TBNPS500 |  |  |  |  | 0.00015322 | 0.0011231 | 0.0032409 | 0.00040909 | 0.0035331 | 0.0019428 | 0.0021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
زهراء المعادي | القطامية | ZHRA.MAADI | KATAMIA | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 12 | 2000/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0.4944 | 3.624 | 4.464e-05 | 1.32 | 11.4 | 2.676e-05 | 7.08 | 2*380/50 ACSR | 12 | [6 empty] | 439 | 440 | 0 | 0 | B_ZHRAA_KATM_1 | ZAHRAA_M | KATAMIA |  |  |  |  | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
زهراء المعادي | القطامية | ZHRA.MAADI | KATAMIA | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR | 12 | 2000/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0.4944 | 3.624 | 4.464e-05 | 1.32 | 11.4 | 2.676e-05 | 7.08 | 2*380/50 ACSR | 12 | [6 empty] | 439 | 440 | 0 | 0 | B_ZHRAA_KATM_2 | ZAHRAA_M | KATAMIA |  |  |  |  | 0.0010215 | 0.0074876 | 0.021606 | 0.0027273 | 0.023554 | 0.012952 | 0.014628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الهضبة 2 | CAIRO.500 | HADABA-II | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 17.93 | 1500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00047678 | 0.0062366 | 0.62153 | 0.0056954 | 0.003889 | 0.52069 | 0 | 0.23076 | 3.0185 | 0.0012841 | 2.7566 | 1.8823 | 0.0010758 | 0 | XLPE 2000mm2 Elswedy | 17.93 | [6 empty] | 400 | 409 | 0 | 0 | B_HDB2_C500_1 | CAIRO500 | HADABA_2 |  |  |  |  | 0.00047678 | 0.0062366 | 0.62153 | 0.0056954 | 0.003889 | 0.52069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الهضبة 2 | CAIRO.500 | HADABA-II | القاهرة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 17.93 | 1500/1 | 2500/1 | 1400 | 533.456 | 1400 | 0.00047678 | 0.0062366 | 0.62153 | 0.0056954 | 0.003889 | 0.52069 | 0 | 0.23076 | 3.0185 | 0.0012841 | 2.7566 | 1.8823 | 0.0010758 | 0 | XLPE 2000mm2 Elswedy | 17.93 | [6 empty] | 400 | 409 | 0 | 0 | B_HDB2_C500_2 | CAIRO500 | HADABA_2 |  |  |  |  | 0.00047678 | 0.0062366 | 0.62153 | 0.0056954 | 0.003889 | 0.52069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 2 | الهرم | HADABA-II | HARAM | القاهرة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy energy | 7.785 | 2500/1 | 1600/1 | 1400 | 533.456 | 1400 | 0.00020701 | 0.0027079 | 0.27223 | 0.0024729 | 0.0010246 | 0.22608 | 0 | 0.10019 | 1.3106 | 0.00056247 | 1.1969 | 0.4959 | 0.0004671 | 0 | XLPE 2000mm2 Elswedy energy | 7.785 | [6 empty] | 409 | 418 | 0 | 0 | B_HDBA2_NHRM | HADABA_2 | N_HARAM |  |  |  |  | 0.00020701 | 0.0027079 | 0.27223 | 0.0024729 | 0.0010246 | 0.22608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 2 | الجيزة | HADABA-II | GIZA | القاهرة | Cable | 1 | 220 | XLPE 1200mm2 Elswedy energy | 14.4 | 2500/1 | 1600/1 | 950 | 361.988 | 950 | 0.00062688 | 0.0050073 | 0.42257 | 0.0065306 | 0.0022344 | 0.36242 | 0 | 0.30341 | 2.4235 | 0.00087307 | 3.1608 | 1.0814 | 0.0007488 | 0 | XLPE 1200mm2 Elswedy energy | 14.4 | [6 empty] | 409 | 416 | 0 | 0 | B_GIZA_HDBA2 | HADABA_2 | GIZA220 |  |  |  |  | 0.00062688 | 0.0050073 | 0.42257 | 0.0065306 | 0.0022344 | 0.36242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | الهضبة 2 | HADABA-I | HADABA-II | القاهرة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 0.435 | 1600/1 | 2500/1 | 1100 | 419.144 | 1200 | 1.0875e-05 | 0.0001092 | 0.0092638 | 0.00018461 | 6.4171e-05 | 0.011159 | 0 | 0.0052635 | 0.052852 | 1.914e-05 | 0.089349 | 0.031059 | 2.3055e-05 | 0 | XLPE 1600mm2 Elswedy | 0.435 | [6 empty] | 408 | 409 | 0 | 0 | B_HDB2_HDB1_1 | HADABA | HADABA_2 |  |  |  |  | 1.0875e-05 | 0.0001092 | 0.0092638 | 0.00018461 | 6.4171e-05 | 0.011159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهضبة 1 | الهضبة 2 | HADABA-I | HADABA-II | القاهرة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 0.435 | 1600/1 | 2500/1 | 1100 | 419.144 | 1200 | 1.0875e-05 | 0.0001092 | 0.0092638 | 0.00018461 | 6.4171e-05 | 0.011159 | 0 | 0.0052635 | 0.052852 | 1.914e-05 | 0.089349 | 0.031059 | 2.3055e-05 | 0 | XLPE 1600mm2 Elswedy | 0.435 | [6 empty] | 408 | 409 | 0 | 0 | B_HDB2_HDB1_2 | HADABA | HADABA_2 |  |  |  |  | 1.0875e-05 | 0.0001092 | 0.0092638 | 0.00018461 | 6.4171e-05 | 0.011159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | صقر قريش | BADR | SKR-KORSH | القاهرة | Circuit & Cable | 1 | 220 | Thermal 1*290/88 XLPE 1200mm2 Elswedy energy 2*405 AAAC XLPE 2000mm2 Elswedy | 41.4 | 2000/1 | 1200/1 | 900 | 342.936 | 950 | 0.0087379 | 0.035194 | 0.16617 | 0.026724 | 0.099059 | 0.13147 | 0.059901 | 4.2291 | 17.0337 | 0.00034332 | 12.9347 | 47.9447 | 0.00027163 | 28.9923 | Thermal 1*290/88 | 35.6 | XLPE 1200mm2 Elswedy energy | 0.47 | 2*405 AAAC | 2.33 | XLPE 2000mm2 Elswedy | 3 | 427 | 428 | 0 | 0 | B_SKR_BDR_1 | BADR | SKRKRISH |  | رئيس قطاع كابلات القاهرة افاد انه يوجد كابلxlp 1200 بين البرجين 32 و 33 تحت فندق تيوليب بتحمل 950 امبير . |  |  | 0.0083974 | 0.032514 | 0.044719 | 0.024933 | 0.09434 | 0.030003 | 0.057061 | 2.0461e-05 | 0.00016343 | 0.013792 | 0.00021315 | 7.2928e-05 | 0.011829 | 0 | 0.00024022 | 0.0014731 | 0.0036651 | 0.00062583 | 0.0039957 | 0.0025148 | 0.0028403 | 7.9773e-05 | 0.0010435 | 0.10399 | 0.00095293 | 0.0006507 | 0.08712 | 0
صقر قريش | غرب الشروق | SKR-KORSH | WST.SHROK | القاهرة | Circuit & Cable | 1 | 220 | Thermal 1*290/88 XLPE 1200mm2 Elswedy energy 2*380/50 ACSR XLPE 2000mm2 Elswedy | 24.77 | 1200/1 | 2500/1 | 900 | 342.936 | 950 | 0.0050793 | 0.020573 | 0.1447 | 0.015942 | 0.056962 | 0.11697 | 0.034025 | 2.4584 | 9.9575 | 0.00029897 | 7.7158 | 27.5698 | 0.00024168 | 16.4683 | Thermal 1*290/88 | 21 | XLPE 1200mm2 Elswedy energy | 0.47 | 2*380/50 ACSR | 0.3 | XLPE 2000mm2 Elswedy | 3 | 428 | 435 | 0 | 0 | B_SKR_WSHR_2 | SKRKRISH | W_SHOROK |  | رئيس قطاع كابلات القاهرة افاد انه يوجد كابلxlp 1200 بين البرجين 32 و 33 تحت فندق تيوليب بتحمل 950 امبير . |  |  | 0.0049535 | 0.019179 | 0.026379 | 0.014707 | 0.05565 | 0.017698 | 0.03366 | 2.0461e-05 | 0.00016343 | 0.013792 | 0.00021315 | 7.2928e-05 | 0.011829 | 0 | 2.5537e-05 | 0.00018719 | 0.00054014 | 6.8182e-05 | 0.00058884 | 0.0003238 | 0.0003657 | 7.9773e-05 | 0.0010435 | 0.10399 | 0.00095293 | 0.0006507 | 0.08712 | 0
بدر | LRT1 | BADR | LRT1 | القناة | Circuit & Cable | 1 | 220 | XLPE 2000mm2 Elswedy 2*380/50 ACSR | 16.3 | 2000/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0013524 | 0.010005 | 0.049066 | 0.0037588 | 0.030946 | 0.034369 | 0.019138 | 0.65456 | 4.8424 | 0.00010138 | 1.8192 | 14.978 | 7.1011e-05 | 9.263 | XLPE 2000mm2 Elswedy | 0.6 | 2*380/50 ACSR | 15.7 |  |  |  |  | 427 | 459 | 0 | 0 | B_LRT1_BADR_1 | BADR | LRT_1 |  |  |  |  | 1.5955e-05 | 0.0002087 | 0.020798 | 0.00019059 | 0.00013014 | 0.017424 | 0 | 0.0013364 | 0.0097963 | 0.028268 | 0.0035682 | 0.030816 | 0.016945 | 0.019138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | LRT1 | BADR | LRT1 | القناة | Circuit & Cable | 2 | 220 | XLPE 2000mm2 Elswedy 2*380/50 ACSR | 16.3 | 2000/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0013524 | 0.010005 | 0.049066 | 0.0037588 | 0.030946 | 0.034369 | 0.019138 | 0.65456 | 4.8424 | 0.00010138 | 1.8192 | 14.978 | 7.1011e-05 | 9.263 | XLPE 2000mm2 Elswedy | 0.6 | 2*380/50 ACSR | 15.7 |  |  |  |  | 427 | 459 | 0 | 0 | B_LRT1_BADR_2 | BADR | LRT_1 |  |  |  |  | 1.5955e-05 | 0.0002087 | 0.020798 | 0.00019059 | 0.00013014 | 0.017424 | 0 | 0.0013364 | 0.0097963 | 0.028268 | 0.0035682 | 0.030816 | 0.016945 | 0.019138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LRT2 | LRT1 | LRT2 | LRT1 | القناة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 0.2 | 2500/1 | 2500/1 | 1600 | 609.664 | 1600 | 5.3182e-06 | 6.9566e-05 | 0.0069328 | 6.3529e-05 | 4.338e-05 | 0.005808 | 0 | 0.002574 | 0.03367 | 1.4324e-05 | 0.030748 | 0.020996 | 1.2e-05 | 0 | XLPE 2000mm2 Elswedy | 0.2 | [6 empty] | 453 | 459 | 0 | 0 | B_LRT1_LRT2_1 | LRT_2 | LRT_1 |  |  |  |  | 5.3182e-06 | 6.9566e-05 | 0.0069328 | 6.3529e-05 | 4.338e-05 | 0.005808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LRT2 | LRT1 | LRT2 | LRT1 | القناة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 0.2 | 2500/1 | 2500/1 | 1600 | 609.664 | 1600 | 5.3182e-06 | 6.9566e-05 | 0.0069328 | 6.3529e-05 | 4.338e-05 | 0.005808 | 0 | 0.002574 | 0.03367 | 1.4324e-05 | 0.030748 | 0.020996 | 1.2e-05 | 0 | XLPE 2000mm2 Elswedy | 0.2 | [6 empty] | 453 | 459 | 0 | 0 | B_LRT1_LRT2_2 | LRT_2 | LRT_1 |  |  |  |  | 5.3182e-06 | 6.9566e-05 | 0.0069328 | 6.3529e-05 | 4.338e-05 | 0.005808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | LRT2 | ASHER-O | LRT2 | القناة | Circuit | 1 | 220 | 3*380/50 ACSR 2*380/50 ACSR | 17.3 | 1600/1 | 2500/1 | 1600 | 609.664 | 1680 | 0.0014203 | 0.010776 | 0.031299 | 0.0042998 | 0.0335 | 0.019106 | 0.020122 | 0.68741 | 5.2155 | 6.4668e-05 | 2.0811 | 16.214 | 3.9476e-05 | 9.739 | 3*380/50 ACSR | 1.3 | 2*380/50 ACSR | 16 |  |  |  |  | 376 | 453 | 0 | 0 |  | 10RAMDAN | LRT_2 |  |  |  |  | 5.8285e-05 | 0.00079236 | 0.0024916 | 0.00066343 | 0.002095 | 0.0018373 | 0.00061777 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | LRT2 | ASHER-O | LRT2 | القناة | Circuit | 2 | 220 | 3*380/50 ACSR 2*380/50 ACSR | 17.3 | 1600/1 | 2500/1 | 1600 | 609.664 | 1680 | 0.0014203 | 0.010776 | 0.031299 | 0.0042998 | 0.0335 | 0.019106 | 0.020122 | 0.68741 | 5.2155 | 6.4668e-05 | 2.0811 | 16.214 | 3.9476e-05 | 9.739 | 3*380/50 ACSR | 1.3 | 2*380/50 ACSR | 16 |  |  |  |  | 376 | 453 | 0 | 0 |  | 10RAMDAN | LRT_2 |  |  |  |  | 5.8285e-05 | 0.00079236 | 0.0024916 | 0.00066343 | 0.002095 | 0.0018373 | 0.00061777 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | غرب الشروق | BADR | WST.SHROK | القاهرة | Circuit | 1 | 220 | Thermal 1*290/88 2*405 AAAC 2*380/50 ACSR | 21.3 | 2000/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.0048463 | 0.019085 | 0.027236 | 0.014344 | 0.055304 | 0.018259 | 0.033642 | 2.3456 | 9.2374 | 5.6273e-05 | 6.9424 | 26.767 | 3.7725e-05 | 16.2825 | Thermal 1*290/88 | 20 | 2*405 AAAC | 1 | 2*380/50 ACSR | 0.3 |  |  | 427 | 435 | 0 | 0 | B_WSH_BDR_1 | BADR | W_SHOROK |  |  |  |  | 0.0047176 | 0.018266 | 0.025123 | 0.014007 | 0.053 | 0.016856 | 0.032057 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 2.5537e-05 | 0.00018719 | 0.00054014 | 6.8182e-05 | 0.00058884 | 0.0003238 | 0.0003657 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | المستقبل | BADR | MOSTKBL | القاهرة | Circuit & Cable | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil XLPE 2000mm2 Elswedy | 19 | 2000/1 | 2500/1 | 1270 | 483.9208 | 1400 | 0.001139 | 0.011431 | 0.21268 | 0.0090373 | 0.02985 | 0.17505 | 0.0063796 | 0.55127 | 5.5325 | 0.00043942 | 4.374 | 14.4472 | 0.00036167 | 3.0877 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 13.5 | XLPE 2000mm2 Elswedy | 5.5 |  |  |  |  | 427 | 483 | 0 | 0 | B_M_CITY_BDR_1 | BADR | M_CITY |  | تم حسابه ب line prop |  |  | 0.00099273 | 0.0095178 | 0.022029 | 0.0072902 | 0.028657 | 0.01533 | 0.0063796 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر | المستقبل | BADR | MOSTKBL | القاهرة | Circuit & Cable | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil XLPE 2000mm2 Elswedy | 19 | 2000/1 | 2500/1 | 1270 | 483.9208 | 1400 | 0.001139 | 0.011431 | 0.21268 | 0.0090373 | 0.02985 | 0.17505 | 0.0063796 | 0.55127 | 5.5325 | 0.00043942 | 4.374 | 14.4472 | 0.00036167 | 3.0877 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 13.5 | XLPE 2000mm2 Elswedy | 5.5 |  |  |  |  | 427 | 483 | 0 | 0 | B_M_CITY_BDR_2 | BADR | M_CITY |  | تم حسابه ب line prop |  |  | 0.00099273 | 0.0095178 | 0.022029 | 0.0072902 | 0.028657 | 0.01533 | 0.0063796 | 0.00014625 | 0.0019131 | 0.19065 | 0.001747 | 0.001193 | 0.15972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوطنية للصلب | الرخام والجرانيت | WTANIA-SOLP | ROKHM&GRNET | القاهرة | Circuit | 1 | 220 | THERMAL 1*357/54 ACSS/TW ,728kcmil 2*405 AAAC | 12.5 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0015906 | 0.0097806 | 0.017639 | 0.0057662 | 0.025659 | 0.012452 | 0.010013 | 0.76984 | 4.7338 | 3.6443e-05 | 2.7908 | 12.4191 | 2.5728e-05 | 4.8461 | THERMAL 1*357/54 ACSS/TW ,728kcmil | 7 | 2*405 AAAC | 5.5 |  |  |  |  | 307 | 311 | 0 | 0 | B_GMRBL_WTNS_1 | WTN_STEL | ROKHAM_G |  | الموصل 2*405 طوله عند الدخول على محطة الرخام والجرانيت 5.5 كم |  |  | 0.0010235 | 0.0063034 | 0.008987 | 0.0042889 | 0.016227 | 0.0065159 | 0.003308 | 0.00056705 | 0.0034773 | 0.0086515 | 0.0014773 | 0.0094318 | 0.0059363 | 0.0067045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوطنية للصلب | الرخام والجرانيت | WTANIA-SOLP | ROKHM&GRNET | القاهرة | Circuit | 2 | 220 | THERMAL 1*357/54 ACSS/TW ,728kcmil 2*405 AAAC | 12.5 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0015906 | 0.0097806 | 0.017639 | 0.0057662 | 0.025659 | 0.012452 | 0.010013 | 0.76984 | 4.7338 | 3.6443e-05 | 2.7908 | 12.4191 | 2.5728e-05 | 4.8461 | THERMAL 1*357/54 ACSS/TW ,728kcmil | 7 | 2*405 AAAC | 5.5 |  |  |  |  | 307 | 311 | 0 | 0 | B_GMRBL_WTNS_2 | WTN_STEL | ROKHAM_G |  | الموصل 2*405 طوله عند الدخول على محطة الرخام والجرانيت 5.5 كم . متنقلة الهيدروجين الاخضر مركبة على هذه الدائرة |  |  | 0.0010235 | 0.0063034 | 0.008987 | 0.0042889 | 0.016227 | 0.0065159 | 0.003308 | 0.00056705 | 0.0034773 | 0.0086515 | 0.0014773 | 0.0094318 | 0.0059363 | 0.0067045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية | الوطنية للصلب | ECTSADIA | WTANIA-SOLP | القناة | Circuit | 1 | 220 | Thermal 1*290/88 2*405 AAAC | 4.4 | 1600/1 | 1600/1 | 1250 | 476.3 | 1300 | 0.00098477 | 0.0039061 | 0.0056538 | 0.0029089 | 0.011286 | 0.0038029 | 0.006899 | 0.47663 | 1.8906 | 1.1681e-05 | 1.4079 | 5.4624 | 7.8571e-06 | 3.3391 | Thermal 1*290/88 | 4 | 2*405 AAAC | 0.4 |  |  |  |  | 306 | 307 | 0 | 0 | B_EKTSD_WTNST1 | EKTASDIA | WTN_STEL |  |  |  |  | 0.00094353 | 0.0036532 | 0.0050246 | 0.0028014 | 0.0106 | 0.0033711 | 0.0064114 | 4.124e-05 | 0.00025289 | 0.0006292 | 0.00010744 | 0.00068595 | 0.00043173 | 0.0004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية | الوطنية للصلب | ECTSADIA | WTANIA-SOLP | القناة | Circuit | 2 | 220 | Thermal 1*290/88 2*405 AAAC | 4.4 | 1600/1 | 1600/1 | 1250 | 476.3 | 1300 | 0.00098477 | 0.0039061 | 0.0056538 | 0.0029089 | 0.011286 | 0.0038029 | 0.006899 | 0.47663 | 1.8906 | 1.1681e-05 | 1.4079 | 5.4624 | 7.8571e-06 | 3.3391 | Thermal 1*290/88 | 4 | 2*405 AAAC | 0.4 |  |  |  |  | 306 | 307 | 0 | 0 | B_EKTSD_WTNST2 | EKTASDIA | WTN_STEL |  |  |  |  | 0.00094353 | 0.0036532 | 0.0050246 | 0.0028014 | 0.0106 | 0.0033711 | 0.0064114 | 4.124e-05 | 0.00025289 | 0.0006292 | 0.00010744 | 0.00068595 | 0.00043173 | 0.0004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | عيون موسى | SUEZ-500 | O.MOUSA | القناة | Circuit | 1 | 220 | 3*490/65 ACSR 2*405 AAAC | 24.7 | 1200/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0011657 | 0.015077 | 0.046997 | 0.012363 | 0.039909 | 0.034574 | 0.012481 | 0.56419 | 7.2975 | 9.7102e-05 | 5.9839 | 19.316 | 7.1434e-05 | 6.041 | 3*490/65 ACSR | 23.7 | 2*405 AAAC | 1 |  |  |  |  | 328 | 344 | 0 | 0 | B_EMSA_SZ50 | SUEZ_500 | EIONMOSA |  | تم جعل الدائرة تحت جهد 220 ك ف وعمل نزلات جديدة boundle للتوصيل على خلايا 220 ك ف وذلك لتقليل حمل محول السويس 500 |  |  | 0.0010626 | 0.014445 | 0.045424 | 0.012095 | 0.038194 | 0.033495 | 0.011262 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 2 | السويس 500 | SUEZ-II | SUEZ-500 | القناة | Circuit | 1 | 220 | 2*405 AAAC | 5 | 1200/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 324 | 328 | 0 | 0 | B_SZ50_SZSS_1 | SUEZSS | SUEZ_500 |  |  |  |  | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 2 | السويس 500 | SUEZ-II | SUEZ-500 | القناة | Circuit | 2 | 220 | 2*405 AAAC | 5 | 1200/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 324 | 328 | 0 | 0 | B_SZ50_SZSS_2 | SUEZSS | SUEZ_500 |  |  |  |  | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | ابو سلطان | SUEZ-500 | ABU-SULT | القناة | Circuit | 1 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 73.9 | 1200/1 | 2000/5 | 500 | 190.52 | 840 | 0.011298 | 0.057713 | 0.10893 | 0.039289 | 0.14505 | 0.079762 | 0.090085 | 5.4685 | 27.9332 | 0.00022506 | 19.016 | 70.205 | 0.0001648 | 43.601 | 1*380/88 ACSR | 57.3 | 2*380/50 ACSR | 16.6 |  |  |  |  | 328 | 372 | 0 | 0 | B_ASUL_SZ50_1 | SUEZ_500 | ABUSLTAN |  |  |  |  | 0.0098854 | 0.047355 | 0.07904 | 0.035517 | 0.11247 | 0.061845 | 0.069849 | 0.0014131 | 0.010358 | 0.029888 | 0.0037727 | 0.032583 | 0.017917 | 0.020236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 500 | ابو سلطان | SUEZ-500 | ABU-SULT | القناة | Circuit | 2 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 73.9 | 1200/1 | 2000/5 | 500 | 190.52 | 840 | 0.011298 | 0.057713 | 0.10893 | 0.039289 | 0.14505 | 0.079762 | 0.090085 | 5.4685 | 27.9332 | 0.00022506 | 19.016 | 70.205 | 0.0001648 | 43.601 | 1*380/88 ACSR | 57.3 | 2*380/50 ACSR | 16.6 |  |  |  |  | 328 | 372 | 0 | 0 | B_ASUL_SZ50_2 | SUEZ_500 | ABUSLTAN |  |  |  |  | 0.0098854 | 0.047355 | 0.07904 | 0.035517 | 0.11247 | 0.061845 | 0.069849 | 0.0014131 | 0.010358 | 0.029888 | 0.0037727 | 0.032583 | 0.017917 | 0.020236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة الجديدة | السويس 500 | N-ATKA | SUEZ-500 | القناة | Circuit | 1 | 220 | 2*405 AAAC | 14 | 2000/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 0.6986 | 4.284 | 4.55e-05 | 1.82 | 11.62 | 3.122e-05 | 8.26 | 2*405 AAAC | 14 | [6 empty] | 321 | 328 | 0 | 0 | B_NATK_SZ50_1 | N_ATAKA | SUEZ_500 |  |  |  |  | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة الجديدة | السويس 500 | N-ATKA | SUEZ-500 | القناة | Circuit | 2 | 220 | 2*405 AAAC | 14 | 2000/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 0.6986 | 4.284 | 4.55e-05 | 1.82 | 11.62 | 3.122e-05 | 8.26 | 2*405 AAAC | 14 | [6 empty] | 321 | 328 | 0 | 0 | B_NATK_SZ50_2 | N_ATAKA | SUEZ_500 |  |  |  |  | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | عتاقة الجديدة | ATAKA | N-ATKA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 1 | 1200/1 | 2000/1 | 1200 | 457.248 | 1600 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0.0499 | 0.306 | 3.25e-06 | 0.13 | 0.83 | 2.23e-06 | 0.59 | 2*405 AAAC | 1 | [6 empty] | 320 | 321 | 0 | 0 | B_NATK_ATAKA_1 | ATAKA1 | N_ATAKA |  |  |  |  | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | عتاقة الجديدة | ATAKA | N-ATKA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 1 | 1200/1 | 2000/1 | 1200 | 457.248 | 1600 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0.0499 | 0.306 | 3.25e-06 | 0.13 | 0.83 | 2.23e-06 | 0.59 | 2*405 AAAC | 1 | [6 empty] | 320 | 321 | 0 | 0 | B_NATK_ATAKA_2 | ATAKA1 | N_ATAKA |  |  |  |  | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | السويس 2 | ATAKA | SUEZ-II | القناة | Circuit | 1 | 220 | 2*236 AAAC 2*405 AAAC | 10 | 1200/1 | 800/1 | 800 | 304.832 | 1200 | 0.0014029 | 0.0064246 | 0.017298 | 0.0045455 | 0.01938 | 0.010793 | 0.01219 | 0.679 | 3.1095 | 3.574e-05 | 2.2 | 9.38 | 2.23e-05 | 5.9 | 2*236 AAAC | 9 | 2*405 AAAC | 1 |  |  |  |  | 320 | 324 | 0 | 0 | B_ATK1_SUEZS_1 | ATAKA1 | SUEZSS |  | محول تيار |  |  | 0.0012998 | 0.0057924 | 0.015725 | 0.0042769 | 0.017665 | 0.0097139 | 0.010971 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | السويس 2 | ATAKA | SUEZ-II | القناة | Circuit | 2 | 220 | 2*236 AAAC 2*405 AAAC | 10 | 1200/1 | 800/1 | 800 | 304.832 | 1200 | 0.0014029 | 0.0064246 | 0.017298 | 0.0045455 | 0.01938 | 0.010793 | 0.01219 | 0.679 | 3.1095 | 3.574e-05 | 2.2 | 9.38 | 2.23e-05 | 5.9 | 2*236 AAAC | 9 | 2*405 AAAC | 1 |  |  |  |  | 320 | 324 | 0 | 0 | B_ATK1_SUEZS_2 | ATAKA1 | SUEZSS |  | محول تيار |  |  | 0.0012998 | 0.0057924 | 0.015725 | 0.0042769 | 0.017665 | 0.0097139 | 0.010971 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 2 | بدر | SUEZ-II | BADR | القناة | Circuit | 1 | 220 | 1*380/88 ACSR | 84 | 800/1 | 2000/1 | 600 | 228.624 | 850 | 0.014492 | 0.069421 | 0.11587 | 0.052066 | 0.16488 | 0.090663 | 0.1024 | 7.014 | 33.6 | 0.0002394 | 25.2 | 79.8 | 0.00018732 | 49.56 | 1*380/88 ACSR | 84 | [6 empty] | 324 | 427 | 0 | 0 | B_SUEZ_BDR_1 | SUEZSS | BADR |  |  |  |  | 0.014492 | 0.069421 | 0.11587 | 0.052066 | 0.16488 | 0.090663 | 0.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس 2 | بدر | SUEZ-II | BADR | القناة | Circuit | 2 | 220 | 1*380/88 ACSR | 84 | 800/1 | 2000/1 | 600 | 228.624 | 850 | 0.014492 | 0.069421 | 0.11587 | 0.052066 | 0.16488 | 0.090663 | 0.1024 | 7.014 | 33.6 | 0.0002394 | 25.2 | 79.8 | 0.00018732 | 49.56 | 1*380/88 ACSR | 84 | [6 empty] | 324 | 427 | 0 | 0 | B_SUEZ_BDR_2 | SUEZSS | BADR |  |  |  |  | 0.014492 | 0.069421 | 0.11587 | 0.052066 | 0.16488 | 0.090663 | 0.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت السويس | عتاقة القديمة | SUEZ.CMNT | ATAKA | القناة | Circuit | 1 | 220 | 2*236 AAAC | 54 | 800/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0077988 | 0.034754 | 0.094351 | 0.025661 | 0.10599 | 0.058283 | 0.065826 | 3.7746 | 16.821 | 0.00019494 | 12.42 | 51.3 | 0.00012042 | 31.86 | 2*236 AAAC | 54 | [6 empty] | 314 | 320 | 0 | 0 | B_ATK2_CMNT_1 | CEMENT | ATAKA2 |  | محول تيار |  |  | 0.0077988 | 0.034754 | 0.094351 | 0.025661 | 0.10599 | 0.058283 | 0.065826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت السويس | عتاقة القديمة | SUEZ.CMNT | ATAKA | القناة | Circuit | 2 | 220 | 2*236 AAAC | 54 | 800/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0077988 | 0.034754 | 0.094351 | 0.025661 | 0.10599 | 0.058283 | 0.065826 | 3.7746 | 16.821 | 0.00019494 | 12.42 | 51.3 | 0.00012042 | 31.86 | 2*236 AAAC | 54 | [6 empty] | 314 | 320 | 0 | 0 | B_ATK2_CMNT_2 | CEMENT | ATAKA2 |  | محول تيار |  |  | 0.0077988 | 0.034754 | 0.094351 | 0.025661 | 0.10599 | 0.058283 | 0.065826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | عروق الصلب | ATAKA | OROOK.SOLP | القناة | Cable | 1 | 220 | CableHpofc 850 | 2.8 | 800/1 | 800/1 | 700 | 266.728 | 800 | 0.00014052 | 0.0010645 | 0.11495 | 0.0014323 | 0.00037366 | 0.074536 | 0 | 0.068012 | 0.5152 | 0.0002375 | 0.69324 | 0.18085 | 0.000154 | 0 | CableHpofc 850 | 2.8 | [6 empty] | 320 | 322 | 0 | 0 | B_ATK2_SOLB_1 | ATAKA2 | E_ELSOLB |  |  |  |  | 0.00014052 | 0.0010645 | 0.11495 | 0.0014323 | 0.00037366 | 0.074536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عتاقة القديمة | عروق الصلب | ATAKA | OROOK.SOLP | القناة | Cable | 2 | 220 | CableHpofc 850 | 2.8 | 800/1 | 800/1 | 700 | 266.728 | 800 | 0.00014052 | 0.0010645 | 0.11495 | 0.0014323 | 0.00037366 | 0.074536 | 0 | 0.068012 | 0.5152 | 0.0002375 | 0.69324 | 0.18085 | 0.000154 | 0 | CableHpofc 850 | 2.8 | [6 empty] | 320 | 322 | 0 | 0 | B_ATK2_SOLB_2 | ATAKA2 | E_ELSOLB |  |  |  |  | 0.00014052 | 0.0010645 | 0.11495 | 0.0014323 | 0.00037366 | 0.074536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صلب السويس | عتاقة القديمة | SOLP-SUEZ | ATAKA | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 4.7 | 2500/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.00040008 | 0.0029326 | 0.0084623 | 0.0010682 | 0.0092252 | 0.0050728 | 0.0057293 | 0.19364 | 1.4194 | 1.7484e-05 | 0.517 | 4.465 | 1.0481e-05 | 2.773 | 2*380/50 ACSR | 4.7 | [6 empty] | 319 | 320 | 0 | 0 | B_ATK2_ELCST_1 | ELCOSTEL | ATAKA2 |  |  |  |  | 0.00040008 | 0.0029326 | 0.0084623 | 0.0010682 | 0.0092252 | 0.0050728 | 0.0057293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
صلب السويس | عتاقة القديمة | SOLP-SUEZ | ATAKA | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 4.7 | 2500/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.00040008 | 0.0029326 | 0.0084623 | 0.0010682 | 0.0092252 | 0.0050728 | 0.0057293 | 0.19364 | 1.4194 | 1.7484e-05 | 0.517 | 4.465 | 1.0481e-05 | 2.773 | 2*380/50 ACSR | 4.7 | [6 empty] | 319 | 320 | 0 | 0 | B_ATK2_ELCST_2 | ELCOSTEL | ATAKA2 |  |  |  |  | 0.00040008 | 0.0029326 | 0.0084623 | 0.0010682 | 0.0092252 | 0.0050728 | 0.0057293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت المصرية | صلب السويس | ELMSRA.CMNT | SOLP-SUEZ | القناة | Circuit | 1 | 220 | 2*380/50 ACSR 2*405 AAAC | 58 | 1600/1 | 2500/1 | 1300 | 495.352 | 1600 | 0.005063 | 0.036248 | 0.10284 | 0.013471 | 0.11211 | 0.062601 | 0.070702 | 2.4505 | 17.544 | 0.00021247 | 6.52 | 54.26 | 0.00012934 | 34.22 | 2*380/50 ACSR | 51 | 2*405 AAAC | 7 |  |  |  |  | 318 | 319 | 0 | 0 | B_ELCST_MSRI_1 | CMNTMSRI | ELCOSTEL |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0.00072169 | 0.0044256 | 0.011011 | 0.0018802 | 0.012004 | 0.0075552 | 0.0085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت المصرية | صلب السويس | ELMSRA.CMNT | SOLP-SUEZ | القناة | Circuit | 2 | 220 | 2*380/50 ACSR 2*405 AAAC | 58 | 1600/1 | 2500/1 | 1300 | 495.352 | 1600 | 0.005063 | 0.036248 | 0.10284 | 0.013471 | 0.11211 | 0.062601 | 0.070702 | 2.4505 | 17.544 | 0.00021247 | 6.52 | 54.26 | 0.00012934 | 34.22 | 2*380/50 ACSR | 51 | 2*405 AAAC | 7 |  |  |  |  | 318 | 319 | 0 | 0 | B_ELCST_MSRI_2 | CMNTMSRI | ELCOSTEL |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0.00072169 | 0.0044256 | 0.011011 | 0.0018802 | 0.012004 | 0.0075552 | 0.0085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنايف | ابوسلطان | MANAIF | ABU-SULT | القناة | Circuit | 1 | 220 | 1*380/88 ACSR | 40 | 800/1 | 2000/5 | 600 | 228.624 | 850 | 0.0069008 | 0.033058 | 0.055176 | 0.024793 | 0.078512 | 0.043173 | 0.04876 | 3.34 | 16 | 0.000114 | 12 | 38 | 8.92e-05 | 23.6 | 1*380/88 ACSR | 40 | [6 empty] | 366 | 372 | 0 | 0 | B_ASUL_MNYF_1 | MANYF | ABUSLTAN |  |  |  |  | 0.0069008 | 0.033058 | 0.055176 | 0.024793 | 0.078512 | 0.043173 | 0.04876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنايف | ابوسلطان | MANAIF | ABU-SULT | القناة | Circuit | 2 | 220 | 1*380/88 ACSR | 40 | 800/1 | 2000/5 | 600 | 228.624 | 850 | 0.0069008 | 0.033058 | 0.055176 | 0.024793 | 0.078512 | 0.043173 | 0.04876 | 3.34 | 16 | 0.000114 | 12 | 38 | 8.92e-05 | 23.6 | 1*380/88 ACSR | 40 | [6 empty] | 366 | 372 | 0 | 0 | B_ASUL_MNYF_2 | MANYF | ABUSLTAN |  |  |  |  | 0.0069008 | 0.033058 | 0.055176 | 0.024793 | 0.078512 | 0.043173 | 0.04876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوسلطان | العاشر الجديدة | ABU-SULT | N.ASHER | القناة | Circuit | 1 | 220 | 2*405 AAAC | 55 | 2000/5 | 1600/1 | 1300 | 495.352 | 1600 | 0.0056705 | 0.034773 | 0.086515 | 0.014773 | 0.094318 | 0.059363 | 0.067045 | 2.7445 | 16.83 | 0.00017875 | 7.15 | 45.65 | 0.00012265 | 32.45 | 2*405 AAAC | 55 | [6 empty] | 372 | 374 | 0 | 0 | B_ASUL_N10R_1 | ABUSLTAN | N_10RAMD |  |  |  |  | 0.0056705 | 0.034773 | 0.086515 | 0.014773 | 0.094318 | 0.059363 | 0.067045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوسلطان | العاشر الجديدة | ABU-SULT | N.ASHER | القناة | Circuit | 2 | 220 | 2*405 AAAC | 55 | 2000/5 | 1600/1 | 1300 | 495.352 | 1600 | 0.0056705 | 0.034773 | 0.086515 | 0.014773 | 0.094318 | 0.059363 | 0.067045 | 2.7445 | 16.83 | 0.00017875 | 7.15 | 45.65 | 0.00012265 | 32.45 | 2*405 AAAC | 55 | [6 empty] | 372 | 374 | 0 | 0 | B_ASUL_N10R_2 | ABUSLTAN | N_10RAMD |  |  |  |  | 0.0056705 | 0.034773 | 0.086515 | 0.014773 | 0.094318 | 0.059363 | 0.067045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عز السويس | اسمنت العربية | EZZ-SUEZ | ELARBA.CMNT | القناة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR | 24.6 | 1600/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.0025237 | 0.015547 | 0.038855 | 0.0065785 | 0.04236 | 0.026551 | 0.029988 | 1.2214 | 7.5248 | 8.0279e-05 | 3.184 | 20.502 | 5.4858e-05 | 14.514 | 2*405 AAAC | 23.9 | 2*380/50 ACSR | 0.7 |  |  |  |  | 310 | 316 | 0 | 0 | B_CMNA_EZDL_1 | EZZ_DL | CMNTARAB |  |  |  |  | 0.0024641 | 0.01511 | 0.037595 | 0.0064194 | 0.040986 | 0.025796 | 0.029134 | 5.9587e-05 | 0.00043678 | 0.0012603 | 0.00015909 | 0.001374 | 0.00075552 | 0.00085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عز السويس | اسمنت العربية | EZZ-SUEZ | ELARBA.CMNT | القناة | Circuit | 2 | 220 | 2*405 AAAC 2*380/50 ACSR | 24.6 | 1600/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.0025237 | 0.015547 | 0.038855 | 0.0065785 | 0.04236 | 0.026551 | 0.029988 | 1.2214 | 7.5248 | 8.0279e-05 | 3.184 | 20.502 | 5.4858e-05 | 14.514 | 2*405 AAAC | 23.9 | 2*380/50 ACSR | 0.7 |  |  |  |  | 310 | 316 | 0 | 0 | B_CMNA_EZDL_2 | EZZ_DL | CMNTARAB |  |  |  |  | 0.0024641 | 0.01511 | 0.037595 | 0.0064194 | 0.040986 | 0.025796 | 0.029134 | 5.9587e-05 | 0.00043678 | 0.0012603 | 0.00015909 | 0.001374 | 0.00075552 | 0.00085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت العربية | اسمنت المصرية | ELARBA.CMNT | ELMSRA.CMNT | القناة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR | 7.3 | 1600/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.00074022 | 0.0046096 | 0.01164 | 0.0019322 | 0.01269 | 0.007879 | 0.0088988 | 0.35827 | 2.231 | 2.4049e-05 | 0.9352 | 6.1418 | 1.6279e-05 | 4.307 | 2*405 AAAC | 6.61 | 2*380/50 ACSR | 0.69 |  |  |  |  | 316 | 318 | 0 | 0 | B_CMNA_CMNM_1 | CMNTARAB | CMNTMSRI |  |  |  |  | 0.00068149 | 0.004179 | 0.010398 | 0.0017754 | 0.011335 | 0.0071343 | 0.0080576 | 5.8736e-05 | 0.00043054 | 0.0012423 | 0.00015682 | 0.0013543 | 0.00074473 | 0.00084112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت العربية | اسمنت المصرية | ELARBA.CMNT | ELMSRA.CMNT | القناة | Circuit | 2 | 220 | 2*405 AAAC 2*380/50 ACSR | 7.3 | 1600/1 | 1600/1 | 1600 | 609.664 | 1600 | 0.00074022 | 0.0046096 | 0.01164 | 0.0019322 | 0.01269 | 0.007879 | 0.0088988 | 0.35827 | 2.231 | 2.4049e-05 | 0.9352 | 6.1418 | 1.6279e-05 | 4.307 | 2*405 AAAC | 6.61 | 2*380/50 ACSR | 0.69 |  |  |  |  | 316 | 318 | 0 | 0 | B_CMNA_CMNM_2 | CMNTARAB | CMNTMSRI |  |  |  |  | 0.00068149 | 0.004179 | 0.010398 | 0.0017754 | 0.011335 | 0.0071343 | 0.0080576 | 5.8736e-05 | 0.00043054 | 0.0012423 | 0.00015682 | 0.0013543 | 0.00074473 | 0.00084112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت المصرية | الجنوب 110 الحربي | ELMSRA.CMNT | GANOUB.110 | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 57.3 | 1600/1 | 2500/1 | 1300 | 495.352 | 1600 | 0.0048776 | 0.035753 | 0.10317 | 0.013023 | 0.11247 | 0.061845 | 0.069849 | 2.3608 | 17.3046 | 0.00021316 | 6.303 | 54.435 | 0.00012778 | 33.807 | 2*380/50 ACSR | 57.3 | [6 empty] | 318 | 441 | 0 | 0 | B_CMNM_KYAN_1 | CMNTMSRI | 110SOUTH |  |  |  |  | 0.0048776 | 0.035753 | 0.10317 | 0.013023 | 0.11247 | 0.061845 | 0.069849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت المصرية | الجنوب 110 الحربي | ELMSRA.CMNT | GANOUB.110 | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 57.3 | 1600/1 | 2500/1 | 1300 | 495.352 | 1600 | 0.0048776 | 0.035753 | 0.10317 | 0.013023 | 0.11247 | 0.061845 | 0.069849 | 2.3608 | 17.3046 | 0.00021316 | 6.303 | 54.435 | 0.00012778 | 33.807 | 2*380/50 ACSR | 57.3 | [6 empty] | 318 | 441 | 0 | 0 | B_CMNM_KYAN_2 | CMNTMSRI | 110SOUTH |  |  |  |  | 0.0048776 | 0.035753 | 0.10317 | 0.013023 | 0.11247 | 0.061845 | 0.069849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القطامية | الجنوب 110 الحربي | KATAMIA | GANOUB.110 | القناة | Circuit | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 11.3 | 1250/1 | 2500/1 | 1250 | 476.3 | 2100 | 0.00083095 | 0.0079668 | 0.018439 | 0.0061022 | 0.023987 | 0.012831 | 0.00534 | 0.40218 | 3.8559 | 3.8097e-05 | 2.9535 | 11.6096 | 2.6511e-05 | 2.5846 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 11.3 | [6 empty] | 440 | 441 | 0 | 0 | B_KAYAN_KTMI_1 | KATAMIA | 110SOUTH |  | محسوبه line prop , محول تيار |  |  | 0.00083095 | 0.0079668 | 0.018439 | 0.0061022 | 0.023987 | 0.012831 | 0.00534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القطامية | الجنوب 110 الحربي | KATAMIA | GANOUB.110 | القناة | Circuit | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 11.3 | 1250/1 | 2500/1 | 1250 | 476.3 | 2100 | 0.00083095 | 0.0079668 | 0.018439 | 0.0061022 | 0.023987 | 0.012831 | 0.00534 | 0.40218 | 3.8559 | 3.8097e-05 | 2.9535 | 11.6096 | 2.6511e-05 | 2.5846 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 11.3 | [6 empty] | 440 | 441 | 0 | 0 | B_KAYAN_KTMI_2 | KATAMIA | 110SOUTH |  | محسوبه line prop , محول تيار |  |  | 0.00083095 | 0.0079668 | 0.018439 | 0.0061022 | 0.023987 | 0.012831 | 0.00534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محطة المجد (العبور 5 سابقا ) | ابوزعبل | Obor 5 | ABO-ZABAL | القناة | Circuit & Cable | 1 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 16.35 | 2500/1 | 2000/1 | 1150 | 438.196 | 1600 | 0.0016589 | 0.010237 | 0.0373 | 0.0044087 | 0.027514 | 0.027433 | 0.019504 | 0.8029 | 4.9549 | 7.7067e-05 | 2.1338 | 13.3167 | 5.668e-05 | 9.44 | 2*405 AAAC | 16 | XLPE 2000mm2 Elswedy | 0.35 |  |  |  |  | 376 | 442 | 0 | 0 | B_OBOUR5_ABZ_1 | OBOUR5 | ABUZABAL |  | جزء الكابل هو الدخول على محطة العبور 5 |  |  | 0.0016496 | 0.010116 | 0.025168 | 0.0042975 | 0.027438 | 0.017269 | 0.019504 | 9.3068e-06 | 0.00012174 | 0.012132 | 0.00011118 | 7.5915e-05 | 0.010164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
محطة المجد (العبور 5 سابقا ) | ابوزعبل | Obor 5 | ABO-ZABAL | القناة | Circuit & Cable | 2 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 16.35 | 2500/1 | 2000/1 | 1150 | 438.196 | 1600 | 0.0016589 | 0.010237 | 0.0373 | 0.0044087 | 0.027514 | 0.027433 | 0.019504 | 0.8029 | 4.9549 | 7.7067e-05 | 2.1338 | 13.3167 | 5.668e-05 | 9.44 | 2*405 AAAC | 16 | XLPE 2000mm2 Elswedy | 0.35 |  |  |  |  | 376 | 442 | 0 | 0 | B_OBOUR5_ABZ_2 | OBOUR5 | ABUZABAL |  | جزء الكابل هو الدخول على محطة العبور 5 |  |  | 0.0016496 | 0.010116 | 0.025168 | 0.0042975 | 0.027438 | 0.017269 | 0.019504 | 9.3068e-06 | 0.00012174 | 0.012132 | 0.00011118 | 7.5915e-05 | 0.010164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | محطة المجد (العبور 5 سابقا ) | ASHER-O | Obor 5 | القناة | Circuit | 1 | 220 | 2*405 AAAC | 36 | 1600/1 | 2500/1 | 1150 | 438.196 | 1600 | 0.0037116 | 0.02276 | 0.056628 | 0.0096694 | 0.061736 | 0.038856 | 0.043884 | 1.7964 | 11.016 | 0.000117 | 4.68 | 29.88 | 8.028e-05 | 21.24 | 2*405 AAAC | 36 | [6 empty] | 376 | 442 | 0 | 0 | B_10RM_OBUR5_1 | 10RAMDAN | OBOUR5 |  |  |  |  | 0.0037116 | 0.02276 | 0.056628 | 0.0096694 | 0.061736 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | محطة المجد (العبور 5 سابقا ) | ASHER-O | Obor 5 | القناة | Circuit | 2 | 220 | 2*405 AAAC | 36 | 1600/1 | 2500/1 | 1150 | 438.196 | 1600 | 0.0037116 | 0.02276 | 0.056628 | 0.0096694 | 0.061736 | 0.038856 | 0.043884 | 1.7964 | 11.016 | 0.000117 | 4.68 | 29.88 | 8.028e-05 | 21.24 | 2*405 AAAC | 36 | [6 empty] | 376 | 442 | 0 | 0 | B_10RM_OBOUR_2 | 10RAMDAN | OBOUR5 |  |  |  |  | 0.0037116 | 0.02276 | 0.056628 | 0.0096694 | 0.061736 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
زيزينيا | بدر 2 | ZEZENIA | BADR-II | القناة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR | 14 | 2500/1 | 2000/1 | 1600 | 609.664 | 1680 | 0.0013715 | 0.0088182 | 0.022932 | 0.003595 | 0.025 | 0.01511 | 0.017066 | 0.6638 | 4.268 | 4.738e-05 | 1.74 | 12.1 | 3.122e-05 | 8.26 | 2*405 AAAC | 10 | 2*380/50 ACSR | 4 |  |  |  |  | 377 | 419 | 0 | 0 |  |  | BADR_2 |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
زيزينيا | بدر 2 | ZEZENIA | BADR-II | القناة | Circuit | 2 | 220 | 2*405 AAAC 2*380/50 ACSR | 14 | 2500/1 | 2000/1 | 1600 | 609.664 | 1680 | 0.0013715 | 0.0088182 | 0.022932 | 0.003595 | 0.025 | 0.01511 | 0.017066 | 0.6638 | 4.268 | 4.738e-05 | 1.74 | 12.1 | 3.122e-05 | 8.26 | 2*405 AAAC | 10 | 2*380/50 ACSR | 4 |  |  |  |  | 377 | 419 | 0 | 0 |  |  | BADR_2 |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | زيزينيا | ASHER-O | ZEZENIA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 5 | 1600/1 | 2500/1 | 1600 | 609.664 | 1680 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 376 | 377 | 0 | 0 |  | 10RAMDAN | [5 empty] | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر القديمة | زيزينيا | ASHER-O | ZEZENIA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 5 | 1600/1 | 2500/1 | 1600 | 609.664 | 1680 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 376 | 377 | 0 | 0 |  | 10RAMDAN | [5 empty] | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر 2 | بدر | BADR-II | BADR | القناة | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR | 13 | 2000/1 | 2000/1 | 1600 | 609.664 | 1680 | 0.0012684 | 0.008186 | 0.021359 | 0.0033264 | 0.023285 | 0.014031 | 0.015847 | 0.6139 | 3.962 | 4.413e-05 | 1.61 | 11.27 | 2.899e-05 | 7.67 | 2*405 AAAC | 9 | 2*380/50 ACSR | 4 |  |  |  |  | 419 | 427 | 0 | 0 | B_BDR2_BDR_1 | BADR_2 | BADR |  |  |  |  | 0.00092789 | 0.0056901 | 0.014157 | 0.0024174 | 0.015434 | 0.0097139 | 0.010971 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بدر 2 | بدر | BADR-II | BADR | القناة | Circuit | 2 | 220 | 2*405 AAAC 2*380/50 ACSR | 13 | 2000/1 | 2000/1 | 1600 | 609.664 | 1680 | 0.0012684 | 0.008186 | 0.021359 | 0.0033264 | 0.023285 | 0.014031 | 0.015847 | 0.6139 | 3.962 | 4.413e-05 | 1.61 | 11.27 | 2.899e-05 | 7.67 | 2*405 AAAC | 9 | 2*380/50 ACSR | 4 |  |  |  |  | 419 | 427 | 0 | 0 | B_BDR2_BDR_2 | BADR_2 | BADR |  |  |  |  | 0.00092789 | 0.0056901 | 0.014157 | 0.0024174 | 0.015434 | 0.0097139 | 0.010971 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر الجديدة | العاشر القديمة | N.ASHER | ASHER-O | القناة | Circuit | 1 | 220 | 2*405 AAAC | 22.5 | 1600/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0023197 | 0.014225 | 0.035393 | 0.0060434 | 0.038585 | 0.024285 | 0.027428 | 1.1227 | 6.885 | 7.3125e-05 | 2.925 | 18.675 | 5.0175e-05 | 13.275 | 2*405 AAAC | 22.5 | [6 empty] | 374 | 376 | 0 | 0 | B_10RM_N10R_1 | N_10RAMD | 10RAMDAN |  | تم فك متنقلة زيزينيا 4 سبتمبر 2022 من على الدائرة |  |  | 0.0023197 | 0.014225 | 0.035393 | 0.0060434 | 0.038585 | 0.024285 | 0.027428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العاشر الجديدة | العاشر القديمة | N.ASHER | ASHER-O | القناة | Circuit | 2 | 220 | 2*405 AAAC | 22.5 | 1600/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0023197 | 0.014225 | 0.035393 | 0.0060434 | 0.038585 | 0.024285 | 0.027428 | 1.1227 | 6.885 | 7.3125e-05 | 2.925 | 18.675 | 5.0175e-05 | 13.275 | 2*405 AAAC | 22.5 | [6 empty] | 374 | 376 | 0 | 0 | B_10RM_N10R_2 | N_10RAMD | 10RAMDAN |  | تم فك متنقلة زيزينيا 4 سبتمبر 2022 من على الدائرة |  |  | 0.0023197 | 0.014225 | 0.035393 | 0.0060434 | 0.038585 | 0.024285 | 0.027428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت السويدي | اسمنت السويس | SWDY.CMNT | SUEZ.CMNT | القناة | Circuit | 1 | 220 | 2*236 AAAC 2*405 AAAC | 3 | 1600/1 | 800/1 | 800 | 304.832 | 1200 | 0.00039194 | 0.0019194 | 0.0050675 | 0.001219 | 0.0056405 | 0.003238 | 0.003657 | 0.1897 | 0.929 | 1.047e-05 | 0.59 | 2.73 | 6.69e-06 | 1.77 | 2*236 AAAC | 2 | 2*405 AAAC | 1 |  |  |  |  | 312 | 314 | 0 | 0 | B_CMNT_CSWD_1 | CMNTSWDY | CEMENT |  |  |  |  | 0.00028884 | 0.0012872 | 0.0034945 | 0.00095041 | 0.0039256 | 0.0021586 | 0.002438 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت السويدي | اسمنت السويس | SWDY.CMNT | SUEZ.CMNT | القناة | Circuit | 2 | 220 | 2*236 AAAC 2*405 AAAC | 3 | 1600/1 | 800/1 | 800 | 304.832 | 1200 | 0.00039194 | 0.0019194 | 0.0050675 | 0.001219 | 0.0056405 | 0.003238 | 0.003657 | 0.1897 | 0.929 | 1.047e-05 | 0.59 | 2.73 | 6.69e-06 | 1.77 | 2*236 AAAC | 2 | 2*405 AAAC | 1 |  |  |  |  | 312 | 314 | 0 | 0 | B_CMNT_CSWD_2 | CMNTSWDY | CEMENT |  |  |  |  | 0.00028884 | 0.0012872 | 0.0034945 | 0.00095041 | 0.0039256 | 0.0021586 | 0.002438 | 0.0001031 | 0.00063223 | 0.001573 | 0.0002686 | 0.0017149 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عز السويس | الاقتصادية 2 | EZZ-SUEZ | EKTESADEYA_2 | القناة | Circuit | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 7.5 | 2500/1 | 2500/1 | 2200 | 838.288 | 2200 | 0.00055152 | 0.0052877 | 0.012238 | 0.0040501 | 0.01592 | 0.0085164 | 0.0035442 | 0.26693 | 2.5592 | 2.5285e-05 | 1.9603 | 7.7055 | 1.7596e-05 | 1.7154 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 7.5 | [6 empty] | 310 |  | 0 | 0 |  | EZZ_DL | [5 empty] | 0.00055152 | 0.0052877 | 0.012238 | 0.0040501 | 0.01592 | 0.0085164 | 0.0035442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عز السويس | الاقتصادية 2 | EZZ-SUEZ | EKTESADEYA_2 | القناة | Circuit | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 7.5 | 2500/1 | 2500/1 | 2200 | 838.288 | 2200 | 0.00055152 | 0.0052877 | 0.012238 | 0.0040501 | 0.01592 | 0.0085164 | 0.0035442 | 0.26693 | 2.5592 | 2.5285e-05 | 1.9603 | 7.7055 | 1.7596e-05 | 1.7154 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 7.5 | [6 empty] | 310 |  | 0 | 0 |  | EZZ_DL | [5 empty] | 0.00055152 | 0.0052877 | 0.012238 | 0.0040501 | 0.01592 | 0.0085164 | 0.0035442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية 2 | اسمنت السويدي | EKTESADEYA_2 | SWDY.CMNT | القناة | Circuit | 1 | 220 | 2*236 AAAC 2*405 AAAC | 6.1 | 2500/1 | 1600/1 | 900 | 342.936 | 1200 | 0.00083552 | 0.0039134 | 0.010467 | 0.0026715 | 0.0117 | 0.0065839 | 0.007436 | 0.40439 | 1.8941 | 2.1625e-05 | 1.293 | 5.663 | 1.3603e-05 | 3.599 | 2*236 AAAC | 5 | 2*405 AAAC | 1.1 | [5 empty] | 312 | 0 | 0 |  |  | CMNTSWDY |  |  |  |  | 0.00072211 | 0.003218 | 0.0087362 | 0.002376 | 0.009814 | 0.0053966 | 0.006095 | 0.00011341 | 0.00069545 | 0.0017303 | 0.00029545 | 0.0018864 | 0.0011873 | 0.0013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية 2 | اسمنت السويدي | EKTESADEYA_2 | SWDY.CMNT | القناة | Circuit | 2 | 220 | 2*236 AAAC 2*405 AAAC | 6.1 | 2500/1 | 1600/1 | 900 | 342.936 | 1200 | 0.00083552 | 0.0039134 | 0.010467 | 0.0026715 | 0.0117 | 0.0065839 | 0.007436 | 0.40439 | 1.8941 | 2.1625e-05 | 1.293 | 5.663 | 1.3603e-05 | 3.599 | 2*236 AAAC | 5 | 2*405 AAAC | 1.1 | [5 empty] | 312 | 0 | 0 |  |  | CMNTSWDY |  |  |  |  | 0.00072211 | 0.003218 | 0.0087362 | 0.002376 | 0.009814 | 0.0053966 | 0.006095 | 0.00011341 | 0.00069545 | 0.0017303 | 0.00029545 | 0.0018864 | 0.0011873 | 0.0013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | السويس BOOT | SOMED.SUEZ | SUZ-BOOT | القناة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 6 | 1200/1 | 1250/1 | 1200 | 457.248 | 1300 | 0.00088416 | 0.0043555 | 0.0088043 | 0.0024751 | 0.01216 | 0.0060028 | 0.0080817 | 0.42793 | 2.1081 | 1.8191e-05 | 1.1979 | 5.8852 | 1.2403e-05 | 3.9115 | Thermal Stacir 1*238/97 | 2 | 2*405 AAAC | 4 |  |  |  |  | 304 | 308 | 0 | 0 | B_SOKHN_SZBT_1 | SOKHNASS | SUEZ_GLF |  |  |  |  | 0.00047176 | 0.0018266 | 0.0025123 | 0.0014007 | 0.0053 | 0.0016856 | 0.0032057 | 0.0004124 | 0.0025289 | 0.006292 | 0.0010744 | 0.0068595 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | السويس BOOT | SOMED.SUEZ | SUZ-BOOT | القناة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 6 | 1200/1 | 1250/1 | 1200 | 457.248 | 1300 | 0.00088416 | 0.0043555 | 0.0088043 | 0.0024751 | 0.01216 | 0.0060028 | 0.0080817 | 0.42793 | 2.1081 | 1.8191e-05 | 1.1979 | 5.8852 | 1.2403e-05 | 3.9115 | Thermal Stacir 1*238/97 | 2 | 2*405 AAAC | 4 |  |  |  |  | 304 | 308 | 0 | 0 | B_SOKHN_SZBT_2 | SOKHNASS | SUEZ_GLF |  |  |  |  | 0.00047176 | 0.0018266 | 0.0025123 | 0.0014007 | 0.0053 | 0.0016856 | 0.0032057 | 0.0004124 | 0.0025289 | 0.006292 | 0.0010744 | 0.0068595 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 1 | الجلالة | ZAFRANA-I | GBL.GLALA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 38 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0039178 | 0.024025 | 0.059774 | 0.010207 | 0.065165 | 0.041014 | 0.046322 | 1.8962 | 11.628 | 0.0001235 | 4.94 | 31.54 | 8.474e-05 | 22.42 | 2*405 AAAC | 38 | [6 empty] | 300 | 305 | 0 | 0 | B_GLALA_ZAF_1 | ZAFARANA | ALGALALA |  |  |  |  | 0.0039178 | 0.024025 | 0.059774 | 0.010207 | 0.065165 | 0.041014 | 0.046322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 1 | الجلالة | ZAFRANA_I | GBL.GLALA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 38 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0039178 | 0.024025 | 0.059774 | 0.010207 | 0.065165 | 0.041014 | 0.046322 | 1.8962 | 11.628 | 0.0001235 | 4.94 | 31.54 | 8.474e-05 | 22.42 | 2*405 AAAC | 38 | [6 empty] | 300 | 305 | 0 | 0 | B_GLALA_ZAF_2 | ZAFARANA | ALGALALA |  |  |  |  | 0.0039178 | 0.024025 | 0.059774 | 0.010207 | 0.065165 | 0.041014 | 0.046322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | الجلالة | SOMED.SUEZ | GBL.GLALA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 24 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0024744 | 0.015174 | 0.037752 | 0.0064463 | 0.041157 | 0.025904 | 0.029256 | 1.1976 | 7.344 | 7.8e-05 | 3.12 | 19.92 | 5.352e-05 | 14.16 | 2*405 AAAC | 24 | [6 empty] | 304 | 305 | 0 | 0 | B_SOKHN_GLAL_1 | SOKHNASS | ALGALALA |  |  |  |  | 0.0024744 | 0.015174 | 0.037752 | 0.0064463 | 0.041157 | 0.025904 | 0.029256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | الجلالة | SOMED.SUEZ | GBL.GLALA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 24 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0024744 | 0.015174 | 0.037752 | 0.0064463 | 0.041157 | 0.025904 | 0.029256 | 1.1976 | 7.344 | 7.8e-05 | 3.12 | 19.92 | 5.352e-05 | 14.16 | 2*405 AAAC | 24 | [6 empty] | 304 | 305 | 0 | 0 | B_SOKHN_GLAL_2 | SOKHNASS | ALGALALA |  |  |  |  | 0.0024744 | 0.015174 | 0.037752 | 0.0064463 | 0.041157 | 0.025904 | 0.029256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | الاقتصادية | SOMED.SUEZ | ECTSADIA | القناة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*405 AAAC 2*380/50 ACSR | 4 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.00046081 | 0.0026612 | 0.0063611 | 0.0012489 | 0.007575 | 0.004199 | 0.0050679 | 0.22303 | 1.288 | 1.3143e-05 | 0.60449 | 3.6663 | 8.6756e-06 | 2.4529 | Thermal Stacir 1*238/97 | 0.5 | 2*405 AAAC | 2.5 | 2*380/50 ACSR | 1 |  |  | 304 | 306 | 0 | 0 | B_EKTS_SOKHN_1 | SOMD_SUZ | EKTASDIA |  |  |  |  | 0.00011794 | 0.00045665 | 0.00062807 | 0.00035018 | 0.001325 | 0.00042139 | 0.00080142 | 0.00025775 | 0.0015806 | 0.0039325 | 0.00067149 | 0.0042872 | 0.0026983 | 0.0030475 | 8.5124e-05 | 0.00062397 | 0.0018005 | 0.00022727 | 0.0019628 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوميد السويس | الاقتصادية | SOMED.SUEZ | ECTSADIA | القناة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*405 AAAC 2*380/50 ACSR | 4 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.00046081 | 0.0026612 | 0.0063611 | 0.0012489 | 0.007575 | 0.004199 | 0.0050679 | 0.22303 | 1.288 | 1.3143e-05 | 0.60449 | 3.6663 | 8.6756e-06 | 2.4529 | Thermal Stacir 1*238/97 | 0.5 | 2*405 AAAC | 2.5 | 2*380/50 ACSR | 1 |  |  | 304 | 306 | 0 | 0 | B_EKTS_SOKHN_2 | SOMD_SUZ | EKTASDIA |  |  |  |  | 0.00011794 | 0.00045665 | 0.00062807 | 0.00035018 | 0.001325 | 0.00042139 | 0.00080142 | 0.00025775 | 0.0015806 | 0.0039325 | 0.00067149 | 0.0042872 | 0.0026983 | 0.0030475 | 8.5124e-05 | 0.00062397 | 0.0018005 | 0.00022727 | 0.0019628 | 0.0010793 | 0.001219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية | السويس BOOT | ECTSADIA | SUZ-BOOT | القناة | Circuit | 1 | 220 | 2*405 AAAC | 4.7 | 1600/1 | 1250/1 | 1250 | 476.3 | 1600 | 0.00048457 | 0.0029715 | 0.0073931 | 0.0012624 | 0.0080599 | 0.0050728 | 0.0057293 | 0.23453 | 1.4382 | 1.5275e-05 | 0.611 | 3.901 | 1.0481e-05 | 2.773 | 2*405 AAAC | 4.7 | [6 empty] | 306 | 308 | 0 | 0 | B_EKTSD_SZBT_1 | EKTASDIA | SUEZ_GLF |  |  |  |  | 0.00048457 | 0.0029715 | 0.0073931 | 0.0012624 | 0.0080599 | 0.0050728 | 0.0057293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقتصادية | السويس BOOT | ECTSADIA | SUZ-BOOT | القناة | Circuit | 2 | 220 | 2*405 AAAC | 4.7 | 1600/1 | 1250/1 | 1250 | 476.3 | 1600 | 0.00048457 | 0.0029715 | 0.0073931 | 0.0012624 | 0.0080599 | 0.0050728 | 0.0057293 | 0.23453 | 1.4382 | 1.5275e-05 | 0.611 | 3.901 | 1.0481e-05 | 2.773 | 2*405 AAAC | 4.7 | [6 empty] | 306 | 308 | 0 | 0 | B_EKTSD_SZBT_2 | EKTASDIA | SUEZ_GLF |  |  |  |  | 0.00048457 | 0.0029715 | 0.0073931 | 0.0012624 | 0.0080599 | 0.0050728 | 0.0057293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوكبير | الجمالية | ABO.KBER | GAMALIA | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 71 | 1600/1 | 2000/1 | 1200 | 457.248 | 1600 | 0.0060438 | 0.044302 | 0.12783 | 0.016136 | 0.13936 | 0.076632 | 0.08655 | 2.9252 | 21.442 | 0.00026412 | 7.81 | 67.45 | 0.00015833 | 41.89 | 2*380/50 ACSR | 71 | [6 empty] | 359 | 506 | 0 | 0 | B_ABKB_GMLI_1 | ABUKBEER | GAMALIA |  |  |  |  | 0.0060438 | 0.044302 | 0.12783 | 0.016136 | 0.13936 | 0.076632 | 0.08655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوكبير | الجمالية | ABO.KBER | GAMALIA | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 71 | 1600/1 | 2000/1 | 1200 | 457.248 | 1600 | 0.0060438 | 0.044302 | 0.12783 | 0.016136 | 0.13936 | 0.076632 | 0.08655 | 2.9252 | 21.442 | 0.00026412 | 7.81 | 67.45 | 0.00015833 | 41.89 | 2*380/50 ACSR | 71 | [6 empty] | 359 | 506 | 0 | 0 | B_ABKB_GMLI_2 | ABUKBEER | GAMALIA |  |  |  |  | 0.0060438 | 0.044302 | 0.12783 | 0.016136 | 0.13936 | 0.076632 | 0.08655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | ابوكبير | SHARKIA | ABO.KBER | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 115 | 1200/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 4.738 | 34.73 | 0.0004278 | 12.65 | 109.25 | 0.00025645 | 67.85 | 2*380/50 ACSR | 115 | [6 empty] | 358 | 359 | 0 | 0 | B_ABKB_SHRK_1 | SHARKIA | ABUKBEER |  |  |  |  | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | ابوكبير | SHARKIA | ABO.KBER | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 115 | 1200/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 4.738 | 34.73 | 0.0004278 | 12.65 | 109.25 | 0.00025645 | 67.85 | 2*380/50 ACSR | 115 | [6 empty] | 358 | 359 | 0 | 0 | B_ABKB_SHRK_2 | SHARKIA | ABUKBEER |  |  |  |  | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | الشباب | SHARKIA | SHABAB | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 32 | 1200/1 | 2000/1 | 1000 | 381.04 | 1600 | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 1.3184 | 9.664 | 0.00011904 | 3.52 | 30.4 | 7.136e-05 | 18.88 | 2*380/50 ACSR | 32 | [6 empty] | 358 | 368 | 0 | 0 | B_SHAB_SHRK_1 | SHARKIA | ALSHABAB |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | الشباب | SHARKIA | SHABAB | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 32 | 1200/1 | 2000/1 | 1000 | 381.04 | 1600 | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 1.3184 | 9.664 | 0.00011904 | 3.52 | 30.4 | 7.136e-05 | 18.88 | 2*380/50 ACSR | 32 | [6 empty] | 358 | 368 | 0 | 0 | B_SHAB_SHRK_2 | SHARKIA | ALSHABAB |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشباب | الزقازيق | SHABAB | ZAGAZIG | القناة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*380/80 ACSR | 47.7 | 2000/1 | 1500/1 | 1000 | 381.04 | 1350 | 0.010694 | 0.042494 | 0.061932 | 0.031656 | 0.12386 | 0.041076 | 0.075035 | 5.1758 | 20.5671 | 0.00012796 | 15.3217 | 59.9494 | 8.4868e-05 | 36.3171 | Thermal Stacir 1*238/97 | 44 | 2*380/80 ACSR | 3.7 |  |  |  |  | 368 | 370 | 0 | 0 | B_SHAB_ZAGZ_1 | ALSHABAB | ZAGAZIG |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.010379 | 0.040185 | 0.05527 | 0.030816 | 0.1166 | 0.037082 | 0.070525 | 0.00031496 | 0.0023087 | 0.0066618 | 0.00084091 | 0.0072624 | 0.0039935 | 0.0045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشباب | الزقازيق | SHABAB | ZAGAZIG | القناة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*380/80 ACSR | 47.7 | 2000/1 | 1500/1 | 1000 | 381.04 | 1350 | 0.010694 | 0.042494 | 0.061932 | 0.031656 | 0.12386 | 0.041076 | 0.075035 | 5.1758 | 20.5671 | 0.00012796 | 15.3217 | 59.9494 | 8.4868e-05 | 36.3171 | Thermal Stacir 1*238/97 | 44 | 2*380/80 ACSR | 3.7 |  |  |  |  | 368 | 370 | 0 | 0 | B_SHAB_ZAGZ_2 | ALSHABAB | ZAGAZIG |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.010379 | 0.040185 | 0.05527 | 0.030816 | 0.1166 | 0.037082 | 0.070525 | 0.00031496 | 0.0023087 | 0.0066618 | 0.00084091 | 0.0072624 | 0.0039935 | 0.0045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنايف | الشباب | MANAIF | SHABAB | القناة | Circuit | 1 | 220 | 2*405 AAAC Thermal Invar 1*255/88 | 33 | 1200/1 | 2000/1 | 1000 | 381.04 | 1300 | 0.0073858 | 0.029296 | 0.042403 | 0.021816 | 0.084645 | 0.028521 | 0.051742 | 3.5747 | 14.1791 | 8.761e-05 | 10.5591 | 40.968 | 5.8929e-05 | 25.0432 | 2*405 AAAC | 3 | Thermal Invar 1*255/88 | 30 |  |  |  |  | 366 | 368 | 0 | 0 | B_MNYF_SHAB_1 | MANYF | ALSHABAB |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.0003093 | 0.0018967 | 0.004719 | 0.00080579 | 0.0051446 | 0.003238 | 0.003657 | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنايف | الشباب | MANAIF | SHABAB | القناة | Circuit | 2 | 220 | 2*405 AAAC Thermal Invar 1*255/88 | 33 | 1200/1 | 2000/1 | 1000 | 381.04 | 1300 | 0.0073858 | 0.029296 | 0.042403 | 0.021816 | 0.084645 | 0.028521 | 0.051742 | 3.5747 | 14.1791 | 8.761e-05 | 10.5591 | 40.968 | 5.8929e-05 | 25.0432 | 2*405 AAAC | 3 | Thermal Invar 1*255/88 | 30 |  |  |  |  | 366 | 368 | 0 | 0 | B_MNYF_SHAB_2 | MANYF | ALSHABAB |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.0003093 | 0.0018967 | 0.004719 | 0.00080579 | 0.0051446 | 0.003238 | 0.003657 | 0.0070765 | 0.027399 | 0.037684 | 0.021011 | 0.0795 | 0.025283 | 0.048085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشباب | العاشر 2 | SHABAB | N.ASHER | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 23.7 | 2000/1 | 1600/1 | 1000 | 381.04 | 1600 | 0.0020174 | 0.014788 | 0.042671 | 0.0053864 | 0.046519 | 0.02558 | 0.02889 | 0.97644 | 7.1574 | 8.8164e-05 | 2.607 | 22.515 | 5.2851e-05 | 13.983 | 2*380/50 ACSR | 23.7 | [6 empty] | 368 | 374 | 0 | 0 | B_N10R_SHAB_1 | ALSHABAB | N_10RAMD |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.0020174 | 0.014788 | 0.042671 | 0.0053864 | 0.046519 | 0.02558 | 0.02889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشباب | العاشر 2 | SHABAB | N.ASHER | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 23.7 | 2000/1 | 1600/1 | 1000 | 381.04 | 1600 | 0.0020174 | 0.014788 | 0.042671 | 0.0053864 | 0.046519 | 0.02558 | 0.02889 | 0.97644 | 7.1574 | 8.8164e-05 | 2.607 | 22.515 | 5.2851e-05 | 13.983 | 2*380/50 ACSR | 23.7 | [6 empty] | 368 | 374 | 0 | 0 | B_N10R_SHAB_2 | ALSHABAB | N_10RAMD |  | يوجد كابل بين القضبان والخط الهوائي 1200 mm يتحمل 950 امبيربمحطة الشباب |  |  | 0.0020174 | 0.014788 | 0.042671 | 0.0053864 | 0.046519 | 0.02558 | 0.02889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الرسوة | المنايف | RASWA | MANAIF | القناة | Circuit | 1 | 220 | 1*380/88 ACSR 1*405 AAAC | 86 | 800/1 | 800/1 | 450 | 171.468 | 800 | 0.014753 | 0.072584 | 0.11607 | 0.053306 | 0.1688 | 0.092822 | 0.10483 | 7.1404 | 35.1308 | 0.00023982 | 25.8 | 81.7 | 0.00019178 | 50.74 | 1*380/88 ACSR | 45.4 | 1*405 AAAC | 40.6 |  |  |  |  | 364 | 366 | 0 | 0 | B_MNYF_RSWA_1 | RASWA | MANYF |  |  |  |  | 0.0078324 | 0.037521 | 0.062625 | 0.02814 | 0.089112 | 0.049001 | 0.055343 | 0.0069205 | 0.035064 | 0.053449 | 0.025165 | 0.07969 | 0.04382 | 0.049492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الرسوة | المنايف | RASWA | MANAIF | القناة | Circuit | 2 | 220 | 1*380/88 ACSR 1*405 AAAC | 86 | 800/1 | 800/1 | 450 | 171.468 | 800 | 0.014753 | 0.072584 | 0.11607 | 0.053306 | 0.1688 | 0.092822 | 0.10483 | 7.1404 | 35.1308 | 0.00023982 | 25.8 | 81.7 | 0.00019178 | 50.74 | 1*380/88 ACSR | 45.4 | 1*405 AAAC | 40.6 |  |  |  |  | 364 | 366 | 0 | 0 | B_MNYF_RSWA_2 | RASWA | MANYF |  |  |  |  | 0.0078324 | 0.037521 | 0.062625 | 0.02814 | 0.089112 | 0.049001 | 0.055343 | 0.0069205 | 0.035064 | 0.053449 | 0.025165 | 0.07969 | 0.04382 | 0.049492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | المنايف | SHARKIA | MANAIF | القناة | Circuit | 1 | 220 | 2*380/50 ACSR 2*405 AAAC | 46 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0042393 | 0.028851 | 0.078727 | 0.011198 | 0.085826 | 0.049649 | 0.056074 | 2.0518 | 13.964 | 0.00016266 | 5.42 | 41.54 | 0.00010258 | 27.14 | 2*380/50 ACSR | 28 | 2*405 AAAC | 18 |  |  |  |  | 358 | 366 | 0 | 0 | B_MNYF_SHRK_1 | SHARKIA | MANYF |  |  |  |  | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 0.0018558 | 0.01138 | 0.028314 | 0.0048347 | 0.030868 | 0.019428 | 0.021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشرقية | المنايف | SHARKIA | MANAIF | القناة | Circuit | 2 | 220 | 2*380/50 ACSR 2*405 AAAC | 46 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0042393 | 0.028851 | 0.078727 | 0.011198 | 0.085826 | 0.049649 | 0.056074 | 2.0518 | 13.964 | 0.00016266 | 5.42 | 41.54 | 0.00010258 | 27.14 | 2*380/50 ACSR | 28 | 2*405 AAAC | 18 |  |  |  |  | 358 | 366 | 0 | 0 | B_MNYF_SHRK_2 | SHARKIA | MANYF |  |  |  |  | 0.0023835 | 0.017471 | 0.050413 | 0.0063636 | 0.054959 | 0.030221 | 0.034132 | 0.0018558 | 0.01138 | 0.028314 | 0.0048347 | 0.030868 | 0.019428 | 0.021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة الجديدة | مدينتي الجديدة | NEWCAIRO | MADINTY | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 19 | 1600/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0.7828 | 5.738 | 7.068e-05 | 2.09 | 18.05 | 4.237e-05 | 11.21 | 2*380/50 ACSR | 19 | [6 empty] | 430 | 481 | 0 | 0 | B_CGAD_MDNTY_1 | CGADIDA | MADENTY |  |  |  |  | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة الجديدة | مدينتي الجديدة | NEWCAIRO | MADINTY | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 19 | 1600/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0.7828 | 5.738 | 7.068e-05 | 2.09 | 18.05 | 4.237e-05 | 11.21 | 2*380/50 ACSR | 19 | [6 empty] | 430 | 481 | 0 | 0 | B_CGAD_MDNTY_2 | CGADIDA | MADENTY |  |  |  |  | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سراي | مدينتي الجديدة | SARAYA | MADINTY | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 4 | 2500/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0.1648 | 1.208 | 1.488e-05 | 0.44 | 3.8 | 8.92e-06 | 2.36 | 2*380/50 ACSR | 4 | [6 empty] | 482 | 481 | 0 | 0 | B_MDNTY_SARY_1 | SARAI | MADENTY |  |  |  |  | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سراي | مدينتي الجديدة | SARAYA | MADINTY | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 4 | 2500/1 | 2500/1 | 1600 | 609.664 | 1600 | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0.1648 | 1.208 | 1.488e-05 | 0.44 | 3.8 | 8.92e-06 | 2.36 | 2*380/50 ACSR | 4 | [6 empty] | 482 | 481 | 0 | 0 | B_MDNTY_SARY_2 | SARAI | MADENTY |  |  |  |  | 0.0003405 | 0.0024959 | 0.0072019 | 0.00090909 | 0.0078512 | 0.0043173 | 0.004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس BOOT | العين السخنة | SUZ-BOOT | EIN-SOKHNA | القناة | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 0.3 | 1250/1 | 2000/1 | 1250 | 476.3 | 1300 | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0 | 0.003861 | 0.050505 | 2.1486e-05 | 0.046122 | 0.031494 | 1.8e-05 | 0 | XLPE 2000mm2 Elswedy | 0.3 | [6 empty] | 308 | 309 | 0 | 0 | B_SOKN_SGLF1 | SUEZ_GLF | AIN_SKHN |  |  |  |  | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السويس BOOT | العين السخنة | SUZ-BOOT | EIN-SOKHNA | القناة | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 0.3 | 1250/1 | 2000/1 | 1250 | 476.3 | 1300 | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0 | 0.003861 | 0.050505 | 2.1486e-05 | 0.046122 | 0.031494 | 1.8e-05 | 0 | XLPE 2000mm2 Elswedy | 0.3 | [6 empty] | 308 | 309 | 0 | 0 | B_SOKNG_SGLF2 | SUEZ_GLF | AIN_SKHN |  |  |  |  | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العين السخنة | سراي | EIN-SOKHNA | SARAYA | القناة | Circuit & Cable | 1 | 220 | 2*405 AAAC Thermal Stacir 1*238/97 2*380/50 ACSR XLPE 2000mm2 Elswedy | 136.3 | 2500/1 | 2000/1 | 1250 | 476.3 | 1300 | 0.013553 | 0.087849 | 0.24263 | 0.036667 | 0.26476 | 0.15337 | 0.16924 | 6.5596 | 42.5188 | 0.0005013 | 17.7469 | 128.1449 | 0.00031688 | 81.912 | 2*405 AAAC | 34 | Thermal Stacir 1*238/97 | 9 | 2*380/50 ACSR | 93 | XLPE 2000mm2 Elswedy | 0.3 | 309 | 482 | 0 | 0 | B_SARAY_SOKN_1 | SARAI | AIN_SKHN |  |  |  |  | 0.0035054 | 0.021496 | 0.053482 | 0.0091322 | 0.058306 | 0.036697 | 0.041446 | 0.0021229 | 0.0082197 | 0.011305 | 0.0063032 | 0.02385 | 0.007585 | 0.014426 | 0.0079165 | 0.058029 | 0.16744 | 0.021136 | 0.18254 | 0.10038 | 0.11337 | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0
العين السخنة | سراي | EIN-SOKHNA | SARAYA | القناة | Circuit & Cable | 2 | 220 | 2*405 AAAC Thermal Stacir 1*238/97 2*380/50 ACSR XLPE 2000mm2 Elswedy | 136.3 | 2500/1 | 2000/1 | 1250 | 476.3 | 1300 | 0.013553 | 0.087849 | 0.24263 | 0.036667 | 0.26476 | 0.15337 | 0.16924 | 6.5596 | 42.5188 | 0.0005013 | 17.7469 | 128.1449 | 0.00031688 | 81.912 | 2*405 AAAC | 34 | Thermal Stacir 1*238/97 | 9 | 2*380/50 ACSR | 93 | XLPE 2000mm2 Elswedy | 0.3 | 309 | 482 | 0 | 0 | B_SARAY_SOKN_2 | SARAI | AIN_SKHN |  |  |  |  | 0.0035054 | 0.021496 | 0.053482 | 0.0091322 | 0.058306 | 0.036697 | 0.041446 | 0.0021229 | 0.0082197 | 0.011305 | 0.0063032 | 0.02385 | 0.007585 | 0.014426 | 0.0079165 | 0.058029 | 0.16744 | 0.021136 | 0.18254 | 0.10038 | 0.11337 | 7.9773e-06 | 0.00010435 | 0.010399 | 9.5293e-05 | 6.507e-05 | 0.008712 | 0
بورسعيد BOOT | الشرقية | P.SAID-E | SHARKIA | القناة | Circuit & Cable | 1 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1600mm2 Elswedy | 100.8 | 1250/1 | 1200/1 | 1100 | 419.144 | 1600 | 0.0090012 | 0.062571 | 0.20427 | 0.024379 | 0.18808 | 0.14565 | 0.12105 | 4.3566 | 30.2845 | 0.00042204 | 11.7995 | 91.0317 | 0.00030094 | 58.587 | 2*405 AAAC | 28.42 | 2*380/50 ACSR | 70.88 | XLPE 1600mm2 Elswedy | 1.5 |  |  | 356 | 358 | 0 | 0 | B_PSBO_SHRK_1 | PS_BOOT | SHARKIA |  | 37.3كم في محافظة الشرقية و 62 كم في محافظة بورسعيد |  |  | 0.0029301 | 0.017968 | 0.044705 | 0.0076335 | 0.048737 | 0.030674 | 0.034644 | 0.0060336 | 0.044227 | 0.12762 | 0.016109 | 0.13912 | 0.076502 | 0.086403 | 3.75e-05 | 0.00037655 | 0.031944 | 0.00063657 | 0.00022128 | 0.038478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بورسعيد BOOT | الشرقية | P.SAID-E | SHARKIA | القناة | Circuit & Cable | 2 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1600mm2 Elswedy | 100.8 | 1250/1 | 1200/1 | 1100 | 419.144 | 1600 | 0.0090012 | 0.062571 | 0.20427 | 0.024379 | 0.18808 | 0.14565 | 0.12105 | 4.3566 | 30.2845 | 0.00042204 | 11.7995 | 91.0317 | 0.00030094 | 58.587 | 2*405 AAAC | 28.42 | 2*380/50 ACSR | 70.88 | XLPE 1600mm2 Elswedy | 1.5 |  |  | 356 | 358 | 0 | 0 | B_PSBO_SHRK_2 | PS_BOOT | SHARKIA |  | 37.3كم في محافظة الشرقية و 62 كم في محافظة بورسعيد |  |  | 0.0029301 | 0.017968 | 0.044705 | 0.0076335 | 0.048737 | 0.030674 | 0.034644 | 0.0060336 | 0.044227 | 0.12762 | 0.016109 | 0.13912 | 0.076502 | 0.086403 | 3.75e-05 | 0.00037655 | 0.031944 | 0.00063657 | 0.00022128 | 0.038478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بورسعيد BOOT | ميناء شرق بورسعيد | P.SAID-E | MINA.PORSID | القناة | Circuit | 1 | 220 | 2*405 AAAC | 30.5 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0031445 | 0.019283 | 0.047976 | 0.0081921 | 0.052304 | 0.032919 | 0.03718 | 1.5219 | 9.333 | 9.9125e-05 | 3.965 | 25.315 | 6.8015e-05 | 17.995 | 2*405 AAAC | 30.5 | [6 empty] | 356 | 357 | 0 | 0 | B_PSAIDEST_BO1 | PS_BOOT | MENA_PS |  |  |  |  | 0.0031445 | 0.019283 | 0.047976 | 0.0081921 | 0.052304 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بورسعيد BOOT | ميناء شرق بورسعيد | P.SAID-E | MINA.PORSID | القناة | Circuit | 2 | 220 | 2*405 AAAC | 30.5 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0031445 | 0.019283 | 0.047976 | 0.0081921 | 0.052304 | 0.032919 | 0.03718 | 1.5219 | 9.333 | 9.9125e-05 | 3.965 | 25.315 | 6.8015e-05 | 17.995 | 2*405 AAAC | 30.5 | [6 empty] | 356 | 357 | 0 | 0 | B_PSAIDEST_BO2 | PS_BOOT | MENA_PS |  |  |  |  | 0.0031445 | 0.019283 | 0.047976 | 0.0081921 | 0.052304 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ميناء شرق بورسعيد | الرسوة | MINA.PORSID | RASWA | القناة | Circuit & Cable | 1 | 220 | 2*405 AAAC XLPE 1600mm2 Elswedy | 29.5 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0029243 | 0.018079 | 0.075988 | 0.0081572 | 0.048238 | 0.068699 | 0.034132 | 1.4154 | 8.7502 | 0.000157 | 3.9481 | 23.3471 | 0.00014194 | 16.52 | 2*405 AAAC | 28 | XLPE 1600mm2 Elswedy | 1.5 |  |  |  |  | 357 | 364 | 0 | 0 | B_PSAIDEST_RS1 | MENA_PS | RASWA |  |  |  |  | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 3.75e-05 | 0.00037655 | 0.031944 | 0.00063657 | 0.00022128 | 0.038478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ميناء شرق بورسعيد | الرسوة | MINA.PORSID | RASWA | القناة | Circuit & Cable | 2 | 220 | 2*405 AAAC XLPE 1600mm2 Elswedy | 29.5 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0029243 | 0.018079 | 0.075988 | 0.0081572 | 0.048238 | 0.068699 | 0.034132 | 1.4154 | 8.7502 | 0.000157 | 3.9481 | 23.3471 | 0.00014194 | 16.52 | 2*405 AAAC | 28 | XLPE 1600mm2 Elswedy | 1.5 |  |  |  |  | 357 | 364 | 0 | 0 | B_PSAIDEST_RS2 | MENA_PS | RASWA |  |  |  |  | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 3.75e-05 | 0.00037655 | 0.031944 | 0.00063657 | 0.00022128 | 0.038478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | بورسعيد BOOT | BER-ABD | P.SAID-E | القناة | Circuit | 1 | 220 | 2*405 AAAC | 61.8 | 1600/1 | 1250/1 | 1250 | 476.3 | 1600 | 0.0063715 | 0.039072 | 0.097211 | 0.016599 | 0.10598 | 0.066702 | 0.075335 | 3.0838 | 18.9108 | 0.00020085 | 8.034 | 51.294 | 0.00013781 | 36.462 | 2*405 AAAC | 61.8 | [6 empty] | 348 | 356 | 0 | 0 | B_BABD_PSBO_1 | BEER_ABD | PS_BOOT |  |  |  |  | 0.0063715 | 0.039072 | 0.097211 | 0.016599 | 0.10598 | 0.066702 | 0.075335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | بورسعيد BOOT | BER-ABD | P.SAID-E | القناة | Circuit | 2 | 220 | 2*405 AAAC | 61.8 | 1600/1 | 1250/1 | 1250 | 476.3 | 1600 | 0.0063715 | 0.039072 | 0.097211 | 0.016599 | 0.10598 | 0.066702 | 0.075335 | 3.0838 | 18.9108 | 0.00020085 | 8.034 | 51.294 | 0.00013781 | 36.462 | 2*405 AAAC | 61.8 | [6 empty] | 348 | 356 | 0 | 0 | B_BABD_PSBO_2 | BEER_ABD | PS_BOOT |  |  |  |  | 0.0063715 | 0.039072 | 0.097211 | 0.016599 | 0.10598 | 0.066702 | 0.075335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البروبلين | الرسوة | PROPLEN | RASWA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 21 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 1.0479 | 6.426 | 6.825e-05 | 2.73 | 17.43 | 4.683e-05 | 12.39 | 2*405 AAAC | 21 | [6 empty] | 360 | 364 | 0 | 0 | B_PROP_RSWA | PROPYLEN | RASWA |  |  |  |  | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ترست | الاثاث | TRUST | ATHATH | القناة | Circuit | 1 | 220 | 2*405 AAAC | 50 | 2000/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.005155 | 0.031612 | 0.07865 | 0.01343 | 0.085744 | 0.053966 | 0.06095 | 2.495 | 15.3 | 0.0001625 | 6.5 | 41.5 | 0.0001115 | 29.5 | 2*405 AAAC | 50 | [6 empty] | 362 | 505 | 0 | 0 | B_ASAS_TRST | TRUST | ELATHATH |  |  |  |  | 0.005155 | 0.031612 | 0.07865 | 0.01343 | 0.085744 | 0.053966 | 0.06095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البروبلين | الاثاث | PROPLEN | ATHATH | القناة | Circuit | 1 | 220 | 2*405 AAAC | 31 | 2000/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.0031961 | 0.019599 | 0.048763 | 0.0083264 | 0.053161 | 0.033459 | 0.037789 | 1.5469 | 9.486 | 0.00010075 | 4.03 | 25.73 | 6.913e-05 | 18.29 | 2*405 AAAC | 31 | [6 empty] | 360 | 505 | 0 | 0 | B_ASAS_PROP | PROPYLEN | ELATHATH |  |  |  |  | 0.0031961 | 0.019599 | 0.048763 | 0.0083264 | 0.053161 | 0.033459 | 0.037789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اولاد حمام | الاثاث | A.HAMAM | ATHATH | القناة | Circuit | 1 | 220 | 2*405 AAAC | 20.6 | 1200/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0021238 | 0.013024 | 0.032404 | 0.0055331 | 0.035326 | 0.022234 | 0.025112 | 1.0279 | 6.3036 | 6.695e-05 | 2.678 | 17.098 | 4.5938e-05 | 12.154 | 2*405 AAAC | 20.6 | [6 empty] | 504 | 505 | 0 | 0 | B_AHMM_ASAS_1 | A_HAMAM | ELATHATH |  |  |  |  | 0.0021238 | 0.013024 | 0.032404 | 0.0055331 | 0.035326 | 0.022234 | 0.025112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اولاد حمام | الاثاث | A.HAMAM | ATHATH | القناة | Circuit | 2 | 220 | 2*405 AAAC | 20.6 | 1200/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0021238 | 0.013024 | 0.032404 | 0.0055331 | 0.035326 | 0.022234 | 0.025112 | 1.0279 | 6.3036 | 6.695e-05 | 2.678 | 17.098 | 4.5938e-05 | 12.154 | 2*405 AAAC | 20.6 | [6 empty] | 504 | 505 | 0 | 0 | B_AHMM_ASAS_2 | A_HAMAM | ELATHATH |  |  |  |  | 0.0021238 | 0.013024 | 0.032404 | 0.0055331 | 0.035326 | 0.022234 | 0.025112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ترست | الرسوة | TRUST | RASWA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 3.233 | 1600/1 | 1600/1 | 1100 | 419.144 | 1600 | 0.00033332 | 0.002044 | 0.0050855 | 0.00086837 | 0.0055442 | 0.0034894 | 0.0039411 | 0.16133 | 0.9893 | 1.0507e-05 | 0.42029 | 2.6834 | 7.2096e-06 | 1.9075 | 2*405 AAAC | 3.233 | [6 empty] | 362 | 364 | 0 | 0 | B_RSWA_TRST | TRUST | RASWA |  |  |  |  | 0.00033332 | 0.002044 | 0.0050855 | 0.00086837 | 0.0055442 | 0.0034894 | 0.0039411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عيون موسى | الاسماعيلية الجديدة | O.MOUSA | ISMAELLIA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 92 | 1200/1 | 2500/1 | 1200 | 457.248 | 1600 | 0.0094851 | 0.058165 | 0.14472 | 0.024711 | 0.15777 | 0.099297 | 0.11215 | 4.5908 | 28.152 | 0.000299 | 11.96 | 76.36 | 0.00020516 | 54.28 | 2*405 AAAC | 92 | [6 empty] | 344 | 345 | 0 | 0 | B_EMSA_ISML_1 | EIONMOSA | ISMALIA |  |  |  |  | 0.0094851 | 0.058165 | 0.14472 | 0.024711 | 0.15777 | 0.099297 | 0.11215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
عيون موسى | الاسماعيلية الجديدة | O.MOUSA | ISMAELLIA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 92 | 1200/1 | 2500/1 | 1200 | 457.248 | 1600 | 0.0094851 | 0.058165 | 0.14472 | 0.024711 | 0.15777 | 0.099297 | 0.11215 | 4.5908 | 28.152 | 0.000299 | 11.96 | 76.36 | 0.00020516 | 54.28 | 2*405 AAAC | 92 | [6 empty] | 344 | 345 | 0 | 0 | B_EMSA_ISML_2 | EIONMOSA | ISMALIA |  |  |  |  | 0.0094851 | 0.058165 | 0.14472 | 0.024711 | 0.15777 | 0.099297 | 0.11215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاسماعيلية الجديدة | القنطرة شرق | ISMAELLIA | KANTRA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 39.5 | 2500/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0040724 | 0.024973 | 0.062133 | 0.01061 | 0.067738 | 0.042633 | 0.048151 | 1.971 | 12.087 | 0.00012837 | 5.135 | 32.785 | 8.8085e-05 | 23.305 | 2*405 AAAC | 39.5 | [6 empty] | 345 | 346 | 0 | 0 | B_ISML_EQNT_1 | ISMALIA | ESTQNTRA |  |  |  |  | 0.0040724 | 0.024973 | 0.062134 | 0.01061 | 0.067738 | 0.042633 | 0.048151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاسماعيلية الجديدة | القنطرة شرق | ISMAELLIA | KANTRA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 39.5 | 2500/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0040724 | 0.024973 | 0.062133 | 0.01061 | 0.067738 | 0.042633 | 0.048151 | 1.971 | 12.087 | 0.00012837 | 5.135 | 32.785 | 8.8085e-05 | 23.305 | 2*405 AAAC | 39.5 | [6 empty] | 345 | 346 | 0 | 0 | B_ISML_EQNT_2 | ISMALIA | ESTQNTRA |  |  |  |  | 0.0040724 | 0.024973 | 0.062134 | 0.01061 | 0.067738 | 0.042633 | 0.048151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس سدر | عيون موسى | RAS-SEDR | O.MOUSA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 43 | NO C.T | 1200/1 | 1200 | 457.248 | 1600 | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 2.1457 | 13.158 | 0.00013975 | 5.59 | 35.69 | 9.589e-05 | 25.37 | 2*405 AAAC | 43 | [6 empty] | 342 | 344 | 0 | 0 | B_EMSA_RASS_1 | RASSEDR | EIONMOSA |  | النزلة لمحطة راس سدر 400 امبير وبالتالي محطة راس سدر لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس سدر | عيون موسى | RAS-SEDR | O.MOUSA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 43 | NO C.T | 1200/1 | 1200 | 457.248 | 1600 | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 2.1457 | 13.158 | 0.00013975 | 5.59 | 35.69 | 9.589e-05 | 25.37 | 2*405 AAAC | 43 | [6 empty] | 342 | 344 | 0 | 0 | B_EMSA_RASS_2 | RASSEDR | EIONMOSA |  | النزلة لمحطة راس سدر 400 امبير وبالتالي محطة راس سدر لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابورديس | راس سدر | ABORDIS | RAS-SEDR | القناة | Circuit | 1 | 220 | 2*405 AAAC | 125 | 1/1600 | NO C.T | 1200 | 457.248 | 1600 | 0.012887 | 0.079029 | 0.19662 | 0.033574 | 0.21436 | 0.13492 | 0.15238 | 6.2375 | 38.25 | 0.00040625 | 16.25 | 103.75 | 0.00027875 | 73.75 | 2*405 AAAC | 125 | [6 empty] | 340 | 342 | 0 | -0.35 | B_RASS_REDS_1 | ABOREDIS | RASSEDR |  | النزلة لمحطة راس سدر 400 امبير وبالتالي محطة راس سدر لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.012887 | 0.079029 | 0.19662 | 0.033574 | 0.21436 | 0.13492 | 0.15238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابورديس | راس سدر | ABORDIS | RAS-SEDR | القناة | Circuit | 2 | 220 | 2*405 AAAC | 125 | 1/1600 | NO C.T | 1200 | 457.248 | 1600 | 0.012887 | 0.079029 | 0.19662 | 0.033574 | 0.21436 | 0.13492 | 0.15238 | 6.2375 | 38.25 | 0.00040625 | 16.25 | 103.75 | 0.00027875 | 73.75 | 2*405 AAAC | 125 | [6 empty] | 340 | 342 | 0 | -0.35 | B_RASS_REDS_2 | ABOREDIS | RASSEDR |  | النزلة لمحطة راس سدر 400 امبير وبالتالي محطة راس سدر لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.012887 | 0.079029 | 0.19662 | 0.033574 | 0.21436 | 0.13492 | 0.15238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الطور | ابورديس | ELTOUR | ABORDIS | القناة | Circuit | 1 | 220 | 2*405 AAAC | 75 | NO C.T | 1/1600 | 1100 | 419.144 | 1600 | 0.0077324 | 0.047417 | 0.11797 | 0.020145 | 0.12862 | 0.080949 | 0.091426 | 3.7425 | 22.95 | 0.00024375 | 9.75 | 62.25 | 0.00016725 | 44.25 | 2*405 AAAC | 75 | [6 empty] | 338 | 340 | 0 | 0 |  | not found in scada | ABOREDIS |  | النزلة لمحطة الطور 400 امبير وبالتالي محطة الطور لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.0077324 | 0.047417 | 0.11797 | 0.020145 | 0.12862 | 0.080949 | 0.091426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الطور | ابورديس | ELTOUR | ABORDIS | القناة | Circuit | 2 | 220 | 2*405 AAAC | 75 | NO C.T | 1/1600 | 1100 | 419.144 | 1600 | 0.0077324 | 0.047417 | 0.11797 | 0.020145 | 0.12862 | 0.080949 | 0.091426 | 3.7425 | 22.95 | 0.00024375 | 9.75 | 62.25 | 0.00016725 | 44.25 | 2*405 AAAC | 75 | [6 empty] | 338 | 340 | 0 | 0 |  | not found in scada | ABOREDIS |  | النزلة لمحطة الطور 400 امبير وبالتالي محطة الطور لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.0077324 | 0.047417 | 0.11797 | 0.020145 | 0.12862 | 0.080949 | 0.091426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | الطور | SHARM | ELTOUR | القناة | Circuit | 1 | 220 | 2*405 AAAC | 107 | 1/1600 | NO C.T | 1100 | 419.144 | 1600 | 0.011032 | 0.067649 | 0.16831 | 0.02874 | 0.18349 | 0.11549 | 0.13043 | 5.3393 | 32.742 | 0.00034775 | 13.91 | 88.81 | 0.00023861 | 63.13 | 2*405 AAAC | 107 | [6 empty] | 330 | 338 | 0 | 0 |  | SHRMSHKH | not found in scada |  | النزلة لمحطة الطور 400 امبير وبالتالي محطة الطور لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.011032 | 0.067649 | 0.16831 | 0.02874 | 0.18349 | 0.11549 | 0.13043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | الطور | SHARM | ELTOUR | القناة | Circuit | 2 | 220 | 2*405 AAAC | 107 | 1/1600 | NO C.T | 1100 | 419.144 | 1600 | 0.011032 | 0.067649 | 0.16831 | 0.02874 | 0.18349 | 0.11549 | 0.13043 | 5.3393 | 32.742 | 0.00034775 | 13.91 | 88.81 | 0.00023861 | 63.13 | 2*405 AAAC | 107 | [6 empty] | 330 | 338 | 0 | 0 |  | SHRMSHKH | not found in scada |  | النزلة لمحطة الطور 400 امبير وبالتالي محطة الطور لاتتحمل اكثر من 400 امبير ولكن ذلك لايؤثر على تحميل الخط نفسه |  |  | 0.011032 | 0.067649 | 0.16831 | 0.02874 | 0.18349 | 0.11549 | 0.13043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القنطرة شرق | بئر العبد | KANTRA | BER-ABD | القناة | Circuit | 1 | 220 | 2*405 AAAC | 68 | 1200/1 | 1200/1 | 1000 | 381.04 | 1600 | 0.0070107 | 0.042992 | 0.10696 | 0.018264 | 0.11661 | 0.073394 | 0.082893 | 3.3932 | 20.808 | 0.000221 | 8.84 | 56.44 | 0.00015164 | 40.12 | 2*405 AAAC | 68 | [6 empty] | 346 | 348 | 0 | 0 | B_BABD_EQNT_1 | ESTQNTRA | BEER_ABD |  |  |  |  | 0.0070107 | 0.042992 | 0.10696 | 0.018264 | 0.11661 | 0.073394 | 0.082893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القنطرة شرق | بئر العبد | KANTRA | BER-ABD | القناة | Circuit | 2 | 220 | 2*405 AAAC | 68 | 1200/1 | 1200/1 | 1000 | 381.04 | 1600 | 0.0070107 | 0.042992 | 0.10696 | 0.018264 | 0.11661 | 0.073394 | 0.082893 | 3.3932 | 20.808 | 0.000221 | 8.84 | 56.44 | 0.00015164 | 40.12 | 2*405 AAAC | 68 | [6 empty] | 346 | 348 | 0 | 0 | B_BABD_EQNT_2 | ESTQNTRA | BEER_ABD |  |  |  |  | 0.0070107 | 0.042992 | 0.10696 | 0.018264 | 0.11661 | 0.073394 | 0.082893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | المساعيد | BER-ABD | MASAEED | القناة | Circuit | 1 | 220 | 2*405 AAAC | 60 | 1200/1 | 2500/1 | 1000 | 381.04 | 1600 | 0.006186 | 0.037934 | 0.09438 | 0.016116 | 0.10289 | 0.064759 | 0.07314 | 2.994 | 18.36 | 0.000195 | 7.8 | 49.8 | 0.0001338 | 35.4 | 2*405 AAAC | 60 | [6 empty] | 348 | 352 | 0 | 0 | B_BABD_MESA_1 | BEER_ABD | M_MASEID |  |  |  |  | 0.006186 | 0.037934 | 0.09438 | 0.016116 | 0.10289 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | المساعيد | BER-ABD | MASAEED | القناة | Circuit | 2 | 220 | 2*405 AAAC | 60 | 1200/1 | 2500/1 | 1000 | 381.04 | 1600 | 0.006186 | 0.037934 | 0.09438 | 0.016116 | 0.10289 | 0.064759 | 0.07314 | 2.994 | 18.36 | 0.000195 | 7.8 | 49.8 | 0.0001338 | 35.4 | 2*405 AAAC | 60 | [6 empty] | 348 | 352 | 0 | 0 | B_BABD_MESA_2 | BEER_ABD | M_MASEID |  |  |  |  | 0.006186 | 0.037934 | 0.09438 | 0.016116 | 0.10289 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المساعيد | العريش | MASAEED | ARISH | القناة | Circuit | 1 | 220 | 2*405 AAAC | 5 | 2500/1 | 750/1 | 1200 | 457.248 | 1600 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 352 | 354 | 0 | 0 | B_ARSH_MESA_1 | M_MASEID | ARISH |  |  |  |  | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المساعيد | العريش | MASAEED | ARISH | القناة | Circuit | 2 | 220 | 2*405 AAAC | 5 | 2500/1 | 750/1 | 1200 | 457.248 | 1600 | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0.2495 | 1.53 | 1.625e-05 | 0.65 | 4.15 | 1.115e-05 | 2.95 | 2*405 AAAC | 5 | [6 empty] | 352 | 354 | 0 | 0 | B_ARSH_MESA_2 | M_MASEID | ARISH |  |  |  |  | 0.0005155 | 0.0031612 | 0.007865 | 0.001343 | 0.0085744 | 0.0053966 | 0.006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | بغداد | BER-ABD | BAGDAD | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 104.7 | 1200/1 | 1/1600 | 1000 | 381.04 | 1600 | 0.0089125 | 0.065329 | 0.18851 | 0.023795 | 0.20551 | 0.113 | 0.12763 | 4.3136 | 31.6194 | 0.00038948 | 11.517 | 99.465 | 0.00023348 | 61.773 | 2*380/50 ACSR | 104.7 | [6 empty] | 348 | 350 | 0 | 0 | B_BAGD_BARD_1 | BEER_ABD | BAGDAD |  |  |  |  | 0.0089125 | 0.065329 | 0.18851 | 0.023795 | 0.20551 | 0.113 | 0.12763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بئر العبد | بغداد | BER-ABD | BAGDAD | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 104.7 | 1200/1 | 1/1600 | 1000 | 381.04 | 1600 | 0.0089125 | 0.065329 | 0.18851 | 0.023795 | 0.20551 | 0.113 | 0.12763 | 4.3136 | 31.6194 | 0.00038948 | 11.517 | 99.465 | 0.00023348 | 61.773 | 2*380/50 ACSR | 104.7 | [6 empty] | 348 | 350 | 0 | 0 | B_BAGD_BARD_2 | BEER_ABD | BAGDAD |  |  |  |  | 0.0089125 | 0.065329 | 0.18851 | 0.023795 | 0.20551 | 0.113 | 0.12763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نويبع | طابا | NWEBEA | TABA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 105 | 1/1600 | 1200/1 | 1200 | 457.248 | 1600 | 0.010825 | 0.066384 | 0.16516 | 0.028202 | 0.18006 | 0.11333 | 0.128 | 5.2395 | 32.13 | 0.00034125 | 13.65 | 87.15 | 0.00023415 | 61.95 | 2*405 AAAC | 105 | [6 empty] | 334 | 336 | 0 | 0 | B_NWBA_TABA_1 | NUWEBAA | TABA |  |  |  |  | 0.010825 | 0.066384 | 0.16517 | 0.028202 | 0.18006 | 0.11333 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نويبع | طابا | NWEBEA | TABA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 105 | 1/1600 | 1200/1 | 1200 | 457.248 | 1600 | 0.010825 | 0.066384 | 0.16516 | 0.028202 | 0.18006 | 0.11333 | 0.128 | 5.2395 | 32.13 | 0.00034125 | 13.65 | 87.15 | 0.00023415 | 61.95 | 2*405 AAAC | 105 | [6 empty] | 334 | 336 | 0 | 0 | B_NWBA_TABA_2 | NUWEBAA | TABA |  |  |  |  | 0.010825 | 0.066384 | 0.16517 | 0.028202 | 0.18006 | 0.11333 | 0.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النبق | نويبع | ELNABQ | NWEBEA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 153 | 1/1600 | 1/1600 | 1250 | 476.3 | 1600 | 0.015774 | 0.096731 | 0.24067 | 0.041095 | 0.26238 | 0.16514 | 0.18651 | 7.6347 | 46.818 | 0.00049725 | 19.89 | 126.99 | 0.00034119 | 90.27 | 2*405 AAAC | 153 | [6 empty] | 332 | 334 | -0.35 | 0 | B_NABQ_NWBA_1 | EL_NABQ | NWEBEA |  |  |  |  | 0.015774 | 0.096731 | 0.24067 | 0.041095 | 0.26238 | 0.16514 | 0.18651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النبق | نويبع | ELNABQ | NWEBEA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 153 | 1/1600 | 1/1600 | 1250 | 476.3 | 1600 | 0.015774 | 0.096731 | 0.24067 | 0.041095 | 0.26238 | 0.16514 | 0.18651 | 7.6347 | 46.818 | 0.00049725 | 19.89 | 126.99 | 0.00034119 | 90.27 | 2*405 AAAC | 153 | [6 empty] | 332 | 334 | -0.35 | 0 | B_NABQ_NWBA_2 | EL_NABQ | NWEBEA |  |  |  |  | 0.015774 | 0.096731 | 0.24067 | 0.041095 | 0.26238 | 0.16514 | 0.18651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد الغردقة | سفاجا | HURGADA-GEN | SAFAGA | القناة | Circuit & Cable | 1 | 220 | 2*405 AAAC XLPE 1600mm2 Elswedy | 48 | 2000/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0045583 | 0.028441 | 0.17412 | 0.013671 | 0.074477 | 0.17467 | 0.052417 | 2.2062 | 13.7655 | 0.00035975 | 6.617 | 36.047 | 0.00036089 | 25.37 | 2*405 AAAC | 43 | XLPE 1600mm2 Elswedy | 5 |  |  |  |  | 397 | 398 | 0 | 0 |  | HERGAD_G | SAFAGA |  |  |  |  | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توليد الغردقة | سفاجا | HURGADA-GEN | SAFAGA | القناة | Circuit & Cable | 2 | 220 | 2*405 AAAC XLPE 1600mm2 Elswedy | 48 | 2000/1 | 1200/1 | 1200 | 457.248 | 1600 | 0.0045583 | 0.028441 | 0.17412 | 0.013671 | 0.074477 | 0.17467 | 0.052417 | 2.2062 | 13.7655 | 0.00035975 | 6.617 | 36.047 | 0.00036089 | 25.37 | 2*405 AAAC | 43 | XLPE 1600mm2 Elswedy | 5 |  |  |  |  | 397 | 398 | 0 | 0 |  | HERGAD_G | SAFAGA |  |  |  |  | 0.0044333 | 0.027186 | 0.067639 | 0.01155 | 0.07374 | 0.046411 | 0.052417 | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القصير | سفاجا | KOSER | SAFAGA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 102.05 | NO C.T | 1200/1 | 1200 | 457.248 | 1600 | 0.010521 | 0.064519 | 0.16052 | 0.02741 | 0.175 | 0.11014 | 0.1244 | 5.0923 | 31.2273 | 0.00033166 | 13.2665 | 84.7015 | 0.00022757 | 60.2095 | 2*405 AAAC | 102.05 | [6 empty] | 396 | 398 | 0 | 0 | B_QOSER_SAFG_1 | QOSEER | SAFAGA |  |  |  |  | 0.010521 | 0.064519 | 0.16052 | 0.02741 | 0.175 | 0.11014 | 0.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القصير | سفاجا | KOSER | SAFAGA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 102.05 | NO C.T | 1200/1 | 1200 | 457.248 | 1600 | 0.010521 | 0.064519 | 0.16052 | 0.02741 | 0.175 | 0.11014 | 0.1244 | 5.0923 | 31.2273 | 0.00033166 | 13.2665 | 84.7015 | 0.00022757 | 60.2095 | 2*405 AAAC | 102.05 | [6 empty] | 396 | 398 | 0 | 0 | B_QOSER_SAFG_2 | QOSEER | SAFAGA |  |  |  |  | 0.010521 | 0.064519 | 0.16052 | 0.02741 | 0.175 | 0.11014 | 0.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مرسى علم | القصير | MRSA.ALAM | KOSER | القناة | Circuit | 1 | 220 | 2*405 AAAC | 146.2 | NO C.T | NO C.T | 1200 | 457.248 | 1600 | 0.015073 | 0.092432 | 0.22997 | 0.039269 | 0.25071 | 0.1578 | 0.17822 | 7.2954 | 44.7372 | 0.00047515 | 19.006 | 121.346 | 0.00032603 | 86.258 | 2*405 AAAC | 146.2 | [6 empty] | 395 | 396 | 0 | 0 | B_QOSER_ALAM_1 | MRS_ALAM | QOSEER |  |  |  |  | 0.015073 | 0.092432 | 0.22997 | 0.039269 | 0.25071 | 0.1578 | 0.17822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مرسى علم | القصير | MRSA.ALAM | KOSER | القناة | Circuit | 2 | 220 | 2*405 AAAC | 146.2 | NO C.T | NO C.T | 1200 | 457.248 | 1600 | 0.015073 | 0.092432 | 0.22997 | 0.039269 | 0.25071 | 0.1578 | 0.17822 | 7.2954 | 44.7372 | 0.00047515 | 19.006 | 121.346 | 0.00032603 | 86.258 | 2*405 AAAC | 146.2 | [6 empty] | 395 | 396 | 0 | 0 | B_QOSER_ALAM_2 | MRS_ALAM | QOSEER |  |  |  |  | 0.015073 | 0.092432 | 0.22997 | 0.039269 | 0.25071 | 0.1578 | 0.17822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب الغردقة | توليد الغردقة | SOTH-HURGDA | HURGADA-GEN | القناة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 5 | 1200/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0.0605 | 0.6075 | 0.00022 | 1.027 | 0.357 | 0.000265 | 0 | XLPE 1600mm2 Elswedy | 5 | [6 empty] | 390 | 397 | 0 | 0 |  | HERGADA | HERGAD_G |  |  |  |  | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب الغردقة | توليد الغردقة | SOTH-HURGDA | HURGADA-GEN | القناة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 5 | 1200/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0.0605 | 0.6075 | 0.00022 | 1.027 | 0.357 | 0.000265 | 0 | XLPE 1600mm2 Elswedy | 5 | [6 empty] | 390 | 397 | 0 | 0 |  | HERGADA | HERGAD_G |  |  |  |  | 0.000125 | 0.0012552 | 0.10648 | 0.0021219 | 0.0007376 | 0.12826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جبل الزيت | شمال الغردقة | GBL.ZEET | NRTH-HURGDA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 110.3 | 1600/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.011372 | 0.069735 | 0.1735 | 0.029626 | 0.18915 | 0.11905 | 0.13446 | 5.504 | 33.7518 | 0.00035847 | 14.339 | 91.549 | 0.00024597 | 65.077 | 2*405 AAAC | 110.3 | [6 empty] | 302 | 392 | -0.25 | 0 | B_GABL_NHERGD1 | GBL_ZAYT | N_HERGDA |  |  |  |  | 0.011372 | 0.069735 | 0.1735 | 0.029626 | 0.18915 | 0.11905 | 0.13446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جبل الزيت | شمال الغردقة | GBL.ZEET | NRTH-HURGDA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 110.3 | 1600/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.011372 | 0.069735 | 0.1735 | 0.029626 | 0.18915 | 0.11905 | 0.13446 | 5.504 | 33.7518 | 0.00035847 | 14.339 | 91.549 | 0.00024597 | 65.077 | 2*405 AAAC | 110.3 | [6 empty] | 302 | 392 | 0 | 0 | B_GABL_NHERGD2 | GBL_ZAYT | N_HERGDA |  |  |  |  | 0.011372 | 0.069735 | 0.1735 | 0.029626 | 0.18915 | 0.11905 | 0.13446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب الغردقة | شمال الغردقة | SOTH-HURGDA | NRTH-HURGDA | القناة | Circuit | 1 | 220 | 2*405 AAAC | 23.7 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0024435 | 0.014984 | 0.03728 | 0.0063657 | 0.040643 | 0.02558 | 0.02889 | 1.1826 | 7.2522 | 7.7025e-05 | 3.081 | 19.671 | 5.2851e-05 | 13.983 | 2*405 AAAC | 23.7 | [6 empty] | 388 | 392 | 0 | 0 | B_NHERGD_HERG1 | HERGADA | N_HERGDA |  |  |  |  | 0.0024435 | 0.014984 | 0.03728 | 0.0063657 | 0.040643 | 0.02558 | 0.02889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب الغردقة | شمال الغردقة | SOTH-HURGDA | NRTH-HURGDA | القناة | Circuit | 2 | 220 | 2*405 AAAC | 23.7 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0024435 | 0.014984 | 0.03728 | 0.0063657 | 0.040643 | 0.02558 | 0.02889 | 1.1826 | 7.2522 | 7.7025e-05 | 3.081 | 19.671 | 5.2851e-05 | 13.983 | 2*405 AAAC | 23.7 | [6 empty] | 388 | 392 | -0.25 | 0 | B_NHERGD_HERG2 | HERGADA | N_HERGDA |  |  |  |  | 0.0024435 | 0.014984 | 0.03728 | 0.0063657 | 0.040643 | 0.02558 | 0.02889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 1 | الزعفرانة 2 | ZAFRANA-I | ZAFRANA-II | القناة | Circuit | 1 | 220 | 2*405 AAAC | 3.7 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.00038147 | 0.0023393 | 0.0058201 | 0.0009938 | 0.006345 | 0.0039935 | 0.0045103 | 0.18463 | 1.1322 | 1.2025e-05 | 0.481 | 3.071 | 8.251e-06 | 2.183 | 2*405 AAAC | 3.7 | [6 empty] | 300 | 301 | 0 | 0 | B_ZAF2_ZAFR_1 | ZAFARANA | ZAFRANA2 |  |  |  |  | 0.00038147 | 0.0023393 | 0.0058201 | 0.0009938 | 0.006345 | 0.0039935 | 0.0045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 1 | الزعفرانة 2 | ZAFRANA-I | ZAFRANA-II | القناة | Circuit | 2 | 220 | 2*405 AAAC | 3.7 | 1200/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.00038147 | 0.0023393 | 0.0058201 | 0.0009938 | 0.006345 | 0.0039935 | 0.0045103 | 0.18463 | 1.1322 | 1.2025e-05 | 0.481 | 3.071 | 8.251e-06 | 2.183 | 2*405 AAAC | 3.7 | [6 empty] | 300 | 301 | 0 | 0 | B_ZAF2_ZAFR_2 | ZAFARANA | ZAFRANA2 |  |  |  |  | 0.00038147 | 0.0023393 | 0.0058201 | 0.0009938 | 0.006345 | 0.0039935 | 0.0045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جبل الزيت | راس غارب | GBL.ZEET | RAS.GHARB | القناة | Circuit | 1 | 220 | 2*405 AAAC | 48.3 | 2000/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0049797 | 0.030537 | 0.075976 | 0.012973 | 0.082829 | 0.052131 | 0.058878 | 2.4102 | 14.7798 | 0.00015698 | 6.279 | 40.089 | 0.00010771 | 28.497 | 2*405 AAAC | 48.3 | [6 empty] | 302 | 303 | 0 | 0 | B_GABL_RGHRB_1 | RS_GHARB | GBL_ZAYT |  |  |  |  | 0.0049797 | 0.030537 | 0.075976 | 0.012973 | 0.082829 | 0.052131 | 0.058878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جبل الزيت | راس غارب | GBL.ZEET | RAS.GHARB | القناة | Circuit | 2 | 220 | 2*405 AAAC | 48.3 | 2000/1 | 1600/1 | 1200 | 457.248 | 1600 | 0.0049797 | 0.030537 | 0.075976 | 0.012973 | 0.082829 | 0.052131 | 0.058878 | 2.4102 | 14.7798 | 0.00015698 | 6.279 | 40.089 | 0.00010771 | 28.497 | 2*405 AAAC | 48.3 | [6 empty] | 302 | 303 | 0 | 0 | B_GABL_RGHRB_2 | RS_GHARB | GBL_ZAYT |  |  |  |  | 0.0049797 | 0.030537 | 0.075976 | 0.012973 | 0.082829 | 0.052131 | 0.058878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 2 | راس غارب | ZAFRANA-II | RAS.GHARB | القناة | Circuit | 1 | 220 | 2*405 AAAC | 123.6 | 1600/1 | 2000/1 | 1300 | 495.352 | 1600 | 0.012743 | 0.078144 | 0.19442 | 0.033198 | 0.21196 | 0.1334 | 0.15067 | 6.1676 | 37.8216 | 0.0004017 | 16.068 | 102.588 | 0.00027563 | 72.924 | 2*405 AAAC | 123.6 | [6 empty] | 301 | 303 | 0 | 0 | B_ZAF2_RGHRB_1 | ZAFRANA2 | RS_GHARB |  |  |  |  | 0.012743 | 0.078144 | 0.19442 | 0.033198 | 0.21196 | 0.1334 | 0.15067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزعفرانة 2 | راس غارب | ZAFRANA-II | RAS.GHARB | القناة | Circuit | 2 | 220 | 2*405 AAAC | 123.6 | 1600/1 | 2000/1 | 1300 | 495.352 | 1600 | 0.012743 | 0.078144 | 0.19442 | 0.033198 | 0.21196 | 0.1334 | 0.15067 | 6.1676 | 37.8216 | 0.0004017 | 16.068 | 102.588 | 0.00027563 | 72.924 | 2*405 AAAC | 123.6 | [6 empty] | 301 | 303 | 0 | 0 | B_ZAF2_RGHRB_2 | ZAFRANA2 | RS_GHARB |  |  |  |  | 0.012743 | 0.078144 | 0.19442 | 0.033198 | 0.21196 | 0.1334 | 0.15067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | النبق | SHARM | ELNABQ | القناة | Circuit | 1 | 220 | 2*405 AAAC | 19 | 1600/1 | 1600/1 | 1300 | 495.352 | 1600 | 0.0019589 | 0.012012 | 0.029887 | 0.0051033 | 0.032583 | 0.020507 | 0.023161 | 0.9481 | 5.814 | 6.175e-05 | 2.47 | 15.77 | 4.237e-05 | 11.21 | 2*405 AAAC | 19 | [6 empty] | 330 | 332 | 0 | 0 | B_NABQ_SHSH_1 | SHRMSHKH | EL_NABQ |  |  |  |  | 0.0019589 | 0.012012 | 0.029887 | 0.0051033 | 0.032583 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | النبق | SHARM | ELNABQ | القناة | Circuit | 2 | 220 | 2*405 AAAC | 19 | 1600/1 | 1600/1 | 1300 | 495.352 | 1600 | 0.0019589 | 0.012012 | 0.029887 | 0.0051033 | 0.032583 | 0.020507 | 0.023161 | 0.9481 | 5.814 | 6.175e-05 | 2.47 | 15.77 | 4.237e-05 | 11.21 | 2*405 AAAC | 19 | [6 empty] | 330 | 332 | 0 | 0 | B_NABQ_SHSH_2 | SHRMSHKH | EL_NABQ |  |  |  |  | 0.0019589 | 0.012012 | 0.029887 | 0.0051033 | 0.032583 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | توليد شرم الشيخ | SHARM | SHARM-GEN | القناة | Cable | 1 | 220 | XLPE 1600mm2 Elswedy | 5.5 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0001375 | 0.0013807 | 0.11713 | 0.0023341 | 0.00081136 | 0.14109 | 0 | 0.06655 | 0.66825 | 0.000242 | 1.1297 | 0.3927 | 0.0002915 | 0 | XLPE 1600mm2 Elswedy | 5.5 | [6 empty] | 330 | 331 | 0 | 0 |  | SHRMSHKH | not found in scada |  | كل كابل من الكابلين موصل على وحدتين والكابلين داخلين على T SECTION بمفتاح على دائرةالنبق / شرم الشيخ رقم 1 داخل محطة شرم الشيخ |  |  | 0.0001375 | 0.0013807 | 0.11713 | 0.0023341 | 0.00081136 | 0.14109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرم الشيخ | توليد شرم الشيخ | SHARM | SHARM-GEN | القناة | Cable | 2 | 220 | XLPE 1600mm2 Elswedy | 5.5 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0001375 | 0.0013807 | 0.11713 | 0.0023341 | 0.00081136 | 0.14109 | 0 | 0.06655 | 0.66825 | 0.000242 | 1.1297 | 0.3927 | 0.0002915 | 0 | XLPE 1600mm2 Elswedy | 5.5 | [6 empty] | 330 | 331 | 0 | 0 |  | SHRMSHKH | not found in scada |  | كل كابل من الكابلين موصل على وحدتين والكابلين داخلين على T SECTION بمفتاح على دائرةالنبق / شرم الشيخ رقم 1 داخل محطة شرم الشيخ |  |  | 0.0001375 | 0.0013807 | 0.11713 | 0.0023341 | 0.00081136 | 0.14109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس غارب | شقير | RAS.GHARB | SHOKAIR | القناة | Circuit | 1 | 220 | 2*405 AAAC | 21 | 2000/1 | 2000/1 | 1600 | 609.664 | 1600 | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 1.0479 | 6.426 | 6.825e-05 | 2.73 | 17.43 | 4.683e-05 | 12.39 | 2*405 AAAC | 21 | [6 empty] | 303 | 313 | 0 | 0 | B_RGH_SHOKR_1 | RS_GHARB | SHOKIR |  |  |  |  | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
راس غارب | شقير | RAS.GHARB | SHOKAIR | القناة | Circuit | 2 | 220 | 2*405 AAAC | 21 | 2000/1 | 2000/1 | 1600 | 609.664 | 1600 | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 1.0479 | 6.426 | 6.825e-05 | 2.73 | 17.43 | 4.683e-05 | 12.39 | 2*405 AAAC | 21 | [6 empty] | 303 | 313 | 0 | 0 | B_RGH_SHOKR_2 | RS_GHARB | SHOKIR |  |  |  |  | 0.0021651 | 0.013277 | 0.033033 | 0.0056405 | 0.036012 | 0.022666 | 0.025599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزقازيق | بهتيم | ZAGAZIG | BAHTEM-I | القناة | Circuit | 1 | 220 | Thermal Stacir 1*238/97 | 59 | 1500/1 | 1200/1 | 1200 | 457.248 | 1300 | 0.013917 | 0.053885 | 0.074113 | 0.041321 | 0.15635 | 0.049724 | 0.094568 | 6.7359 | 26.0802 | 0.00015313 | 19.9993 | 75.6734 | 0.00010274 | 45.7707 | Thermal Stacir 1*238/97 | 59 | [6 empty] | 370 | 476 | 0 | 0 | B_BHTM_ZAGZ_1 | ZAGAZIG | BAHTEEM |  | الخط يتبع محافظة الشرقية |  |  | 0.013917 | 0.053885 | 0.074113 | 0.041321 | 0.15635 | 0.049724 | 0.094568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزقازيق | بهتيم | ZAGAZIG | BAHTEM-I | القناة | Circuit | 2 | 220 | Thermal Stacir 1*238/97 | 59 | 1500/1 | 1200/1 | 1200 | 457.248 | 1300 | 0.013917 | 0.053885 | 0.074113 | 0.041321 | 0.15635 | 0.049724 | 0.094568 | 6.7359 | 26.0802 | 0.00015313 | 19.9993 | 75.6734 | 0.00010274 | 45.7707 | Thermal Stacir 1*238/97 | 59 | [6 empty] | 370 | 476 | 0 | 0 | B_BHTM_ZAGZ_2 | ZAGAZIG | BAHTEEM |  | الخط يتبع محافظة الشرقية |  |  | 0.013917 | 0.053885 | 0.074113 | 0.041321 | 0.15635 | 0.049724 | 0.094568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طلخا | ربط (طلخا, المحلة, ميت غمر) | TALKHA | JB(TL-MG-MH) | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 19.3 | 1000/1 | NO C.T | 1000 | 381.04 | 1200 | 0.0016429 | 0.012043 | 0.034749 | 0.0043864 | 0.037882 | 0.020831 | 0.023527 | 0.79516 | 5.8286 | 7.1796e-05 | 2.123 | 18.335 | 4.3039e-05 | 11.387 | 2*380/50 ACSR | 19.3 | [6 empty] | 512 | 519 | 0 | 0 | B_RBT_TLKHA1 | TALKHA1 | RBT_GHMR |  | محولات التيار |  |  | 0.0016429 | 0.012043 | 0.034749 | 0.0043864 | 0.037882 | 0.020831 | 0.023527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحلة | ربط (طلخا, المحلة, ميت غمر) | MEHALA | JB(TL-MG-MH) | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 6.3 | 1200/1 | NO C.T | 1200 | 457.248 | 1200 | 0.00053628 | 0.003931 | 0.011343 | 0.0014318 | 0.012366 | 0.0067997 | 0.0076798 | 0.25956 | 1.9026 | 2.3436e-05 | 0.693 | 5.985 | 1.4049e-05 | 3.717 | 2*380/50 ACSR | 6.3 | [6 empty] | 518 | 519 | 0 | 0 | B_RBT_MHLA | MEHALLA | RBT_GHMR |  |  |  |  | 0.00053628 | 0.003931 | 0.011343 | 0.0014318 | 0.012366 | 0.0067997 | 0.0076798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ميت غمر | ربط (طلخا, المحلة, ميت غمر) | MET-GHAMR | JB(TL-MG-MH) | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 24 | 1600/1 | NO C.T | 1200 | 457.248 | 1200 | 0.002043 | 0.014975 | 0.043212 | 0.0054545 | 0.047107 | 0.025904 | 0.029256 | 0.9888 | 7.248 | 8.928e-05 | 2.64 | 22.8 | 5.352e-05 | 14.16 | 2*380/50 ACSR | 24 | [6 empty] | 517 | 519 | 0 | 0 | B_RBT_GHMR | MEETGHMR | RBT_GHMR |  |  |  |  | 0.002043 | 0.014975 | 0.043212 | 0.0054545 | 0.047107 | 0.025904 | 0.029256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طلخا | ميت غمر | TALKHA | MET-GHAMR | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 43.3 | 1000/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0036859 | 0.027018 | 0.077961 | 0.0098409 | 0.08499 | 0.046735 | 0.052783 | 1.784 | 13.0766 | 0.00016108 | 4.763 | 41.135 | 9.6559e-05 | 25.547 | 2*380/50 ACSR | 43.3 | [6 empty] | 512 | 517 | 0 | 0 | B_GHMR_TLK1_2 | TALKHA1 | MEETGHMR |  | محولات التيار |  |  | 0.0036859 | 0.027018 | 0.077961 | 0.0098409 | 0.08499 | 0.046735 | 0.052783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طلخا | كفر الشيخ القديمة | TALKHA | KAFR-SHEKH | وسط الدلتا | Circuit | 1 | 220 | Thermal Stacir 1*238/97 | 55 | 2000/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.012974 | 0.050232 | 0.069088 | 0.038519 | 0.14575 | 0.046353 | 0.088156 | 6.2792 | 24.3121 | 0.00014274 | 18.6434 | 70.543 | 9.5771e-05 | 42.6676 | Thermal Stacir 1*238/97 | 55 | [6 empty] | 512 | 514 | 0 | 0 | B_KSHI_TLK1_1 | TALKHA1 | KSHIEKH |  |  |  |  | 0.012974 | 0.050232 | 0.069088 | 0.038519 | 0.14575 | 0.046353 | 0.088156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طلخا | كفر الشيخ القديمة | TALKHA | KAFR-SHEKH | وسط الدلتا | Circuit | 2 | 220 | Thermal Stacir 1*238/97 | 55 | 2000/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.012974 | 0.050232 | 0.069088 | 0.038519 | 0.14575 | 0.046353 | 0.088156 | 6.2792 | 24.3121 | 0.00014274 | 18.6434 | 70.543 | 9.5771e-05 | 42.6676 | Thermal Stacir 1*238/97 | 55 | [6 empty] | 512 | 514 | 0 | 0 | B_KSHI_TLK1_2 | TALKHA1 | KSHIEKH |  |  |  |  | 0.012974 | 0.050232 | 0.069088 | 0.038519 | 0.14575 | 0.046353 | 0.088156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سندوب | طلخا | SANDOOB | TALKHA | وسط الدلتا | Circuit | 1 | 220 | 2*507 AAAC | 12 | 1600/1 | 1600/5 | 1600 | 609.664 | 1700 | 0.00091736 | 0.0073884 | 0.021838 | 0.0094215 | 0.023554 | 0.012952 | 0.014628 | 0.444 | 3.576 | 4.512e-05 | 4.56 | 11.4 | 2.676e-05 | 7.08 | 2*507 AAAC | 12 | [6 empty] | 511 | 512 | 0 | 0 | B_SNDOB_TLK2_1 | SANDOB | TALKHA2 |  | CT at talkha 5/1600/2000 and 1600 is selected |  |  | 0.00091736 | 0.0073884 | 0.021838 | 0.0094215 | 0.023554 | 0.012952 | 0.014628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سندوب | طلخا | SANDOOB | TALKHA | وسط الدلتا | Circuit | 2 | 220 | 2*507 AAAC | 12 | 1600/1 | 1600/5 | 1600 | 609.664 | 1700 | 0.00091736 | 0.0073884 | 0.021838 | 0.0094215 | 0.023554 | 0.012952 | 0.014628 | 0.444 | 3.576 | 4.512e-05 | 4.56 | 11.4 | 2.676e-05 | 7.08 | 2*507 AAAC | 12 | [6 empty] | 511 | 512 | 0 | 0 | B_SNDOB_TLK2_2 | SANDOB | TALKHA2 |  | CT at talkha 5/1600/2000 and 1600 is selected |  |  | 0.00091736 | 0.0073884 | 0.021838 | 0.0094215 | 0.023554 | 0.012952 | 0.014628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجمالية | غرب دمياط | GAMALIA | W.DOMIAT | وسط الدلتا | Circuit | 1 | 220 | 2*507 AAAC Thermal Double Stacir 2*238/97 | 50 | 2000/1 | 2000/1 | 1615 | 615.3796 | 1700 | 0.0052038 | 0.033484 | 0.084685 | 0.032579 | 0.1137 | 0.051826 | 0.073618 | 2.5186 | 16.2064 | 0.00017497 | 15.7683 | 55.0304 | 0.00010708 | 35.6309 | 2*507 AAAC | 17 | Thermal Double Stacir 2*238/97 | 33 |  |  |  |  | 506 | 507 | 0 | 0 | B_GMLI_WDMIT_1 | GAMALIA | WDAMITTA |  |  |  |  | 0.0012996 | 0.010467 | 0.030937 | 0.013347 | 0.033368 | 0.018348 | 0.020723 | 0.0039042 | 0.023017 | 0.053748 | 0.019232 | 0.080331 | 0.033478 | 0.052894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الجمالية | غرب دمياط | GAMALIA | W.DOMIAT | وسط الدلتا | Circuit | 2 | 220 | 2*507 AAAC Thermal Double Stacir 2*238/97 | 50 | 2000/1 | 2000/1 | 1615 | 615.3796 | 1700 | 0.0052038 | 0.033484 | 0.084685 | 0.032579 | 0.1137 | 0.051826 | 0.073618 | 2.5186 | 16.2064 | 0.00017497 | 15.7683 | 55.0304 | 0.00010708 | 35.6309 | 2*507 AAAC | 17 | Thermal Double Stacir 2*238/97 | 33 |  |  |  |  | 506 | 507 | 0 | 0 | B_GMLI_WDMIT_2 | GAMALIA | WDAMITTA |  |  |  |  | 0.0012996 | 0.010467 | 0.030937 | 0.013347 | 0.033368 | 0.018348 | 0.020723 | 0.0039042 | 0.023017 | 0.053748 | 0.019232 | 0.080331 | 0.033478 | 0.052894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جمصة | المنصورة الجديدة | GAMASA | MANSORA-NEW | وسط الدلتا | Circuit | 1 | 220 | Thermal Double 2*255/98 ACSS | 11.26 | 1600/1 | 2500/1 | 1600 | 609.664 | 2500 | 0.0013322 | 0.0078538 | 0.018339 | 0.0065622 | 0.02741 | 0.011423 | 0.018048 | 0.64477 | 3.8012 | 3.7891e-05 | 3.1761 | 13.2665 | 2.3601e-05 | 8.7353 | Thermal Double 2*255/98 ACSS | 11.26 | [6 empty] | 509 | 510 | 0 | 0 |  | GAMASA20 | MANSOURA |  | محول تيار |  |  | 0.0013322 | 0.0078538 | 0.018339 | 0.0065622 | 0.02741 | 0.011423 | 0.018048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جمصة | المنصورة الجديدة | GAMASA | MANSORA-NEW | وسط الدلتا | Circuit | 2 | 220 | Thermal Double 2*255/98 ACSS | 11.26 | 1600/1 | 2500/1 | 1600 | 609.664 | 2500 | 0.0013322 | 0.0078538 | 0.018339 | 0.0065622 | 0.02741 | 0.011423 | 0.018048 | 0.64477 | 3.8012 | 3.7891e-05 | 3.1761 | 13.2665 | 2.3601e-05 | 8.7353 | Thermal Double 2*255/98 ACSS | 11.26 | [6 empty] | 509 | 510 | 0 | 0 |  | GAMASA20 | MANSOURA |  | محول تيار |  |  | 0.0013322 | 0.0078538 | 0.018339 | 0.0065622 | 0.02741 | 0.011423 | 0.018048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع غرب دمياط | جمصة | N.W.DOM-GEN | GAMASA | وسط الدلتا | Circuit | 1 | 220 | Thermal Double 2*255/98 | 11 | 2000/1 | 1600/1 | 1600 | 609.664 | 2400 | 0.0013014 | 0.0076725 | 0.017916 | 0.0064107 | 0.026777 | 0.011159 | 0.017631 | 0.62988 | 3.7135 | 3.7017e-05 | 3.1028 | 12.9601 | 2.3056e-05 | 8.5336 | Thermal Double 2*255/98 | 11 | [6 empty] | 508 | 509 | 0 | 0 | B_WDMT2_GMSA_1 | WDMTTA_2 | GAMASA20 |  | محول تيار |  |  | 0.0013014 | 0.0076725 | 0.017916 | 0.0064107 | 0.026777 | 0.011159 | 0.017631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع غرب دمياط | جمصة | N.W.DOM-GEN | GAMASA | وسط الدلتا | Circuit | 2 | 220 | Thermal Double 2*255/98 | 11 | 2000/1 | 1600/1 | 1600 | 609.664 | 2400 | 0.0013014 | 0.0076725 | 0.017916 | 0.0064107 | 0.026777 | 0.011159 | 0.017631 | 0.62988 | 3.7135 | 3.7017e-05 | 3.1028 | 12.9601 | 2.3056e-05 | 8.5336 | Thermal Double 2*255/98 | 11 | [6 empty] | 508 | 509 | 0 | 0 |  | WDMTTA_2 | GAMASA20 |  | محول تيار |  |  | 0.0013014 | 0.0076725 | 0.017916 | 0.0064107 | 0.026777 | 0.011159 | 0.017631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط | دمياط الجديدة | DOMIAAT | NEW-DOMT | وسط الدلتا | Circuit | 1 | 220 | Thermal Double Stacir 2*238/97 | 0.5 | 2000/1 | 2000/1 | 2000 | 762.08 | 2400 | 5.9155e-05 | 0.00034875 | 0.00081436 | 0.00029139 | 0.0012171 | 0.00050724 | 0.00080143 | 0.028631 | 0.16879 | 1.6826e-06 | 0.14103 | 0.5891 | 1.048e-06 | 0.38789 | Thermal Double Stacir 2*238/97 | 0.5 | [6 empty] | 500 | 502 | 0 | 0 | B_DMTP_NDMT_1 | DEMITAPS | NDAMITTA |  | محول تيار |  |  | 5.9155e-05 | 0.00034875 | 0.00081436 | 0.00029139 | 0.0012171 | 0.00050724 | 0.00080143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط | دمياط الجديدة | DOMIAAT | NEW-DOMT | وسط الدلتا | Circuit | 2 | 220 | Thermal Double Stacir 2*238/97 | 0.5 | 2000/1 | 2000/1 | 2000 | 762.08 | 2400 | 5.9155e-05 | 0.00034875 | 0.00081436 | 0.00029139 | 0.0012171 | 0.00050724 | 0.00080143 | 0.028631 | 0.16879 | 1.6826e-06 | 0.14103 | 0.5891 | 1.048e-06 | 0.38789 | Thermal Double Stacir 2*238/97 | 0.5 | [6 empty] | 500 | 502 | 0 | 0 | B_DMTP_NDMT_2 | DEMITAPS | NDAMITTA |  | محول تيار |  |  | 5.9155e-05 | 0.00034875 | 0.00081436 | 0.00029139 | 0.0012171 | 0.00050724 | 0.00080143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط الجديدة | اولاد حمام | NEW-DOMT | A.HAMAM | وسط الدلتا | Circuit | 1 | 220 | Thermal Double Stacir 2*238/97 | 8 | 2000/1 | 2000/1 | 2000 | 762.08 | 2400 | 0.00094648 | 0.00558 | 0.01303 | 0.0046623 | 0.019474 | 0.0081159 | 0.012823 | 0.45809 | 2.7007 | 2.6921e-05 | 2.2566 | 9.4255 | 1.6768e-05 | 6.2063 | Thermal Double Stacir 2*238/97 | 8 | [6 empty] | 502 | 504 | 0 | 0 | B_AHMM_NDMT_1 | NDAMITTA | A_HAMAM |  | محول تيار |  |  | 0.00094648 | 0.00558 | 0.01303 | 0.0046623 | 0.019474 | 0.0081159 | 0.012823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط الجديدة | اولاد حمام | NEW-DOMT | A.HAMAM | وسط الدلتا | Circuit | 2 | 220 | Thermal Double Stacir 2*238/97 | 8 | 2000/1 | 2000/1 | 2000 | 762.08 | 2400 | 0.00094648 | 0.00558 | 0.01303 | 0.0046623 | 0.019474 | 0.0081159 | 0.012823 | 0.45809 | 2.7007 | 2.6921e-05 | 2.2566 | 9.4255 | 1.6768e-05 | 6.2063 | Thermal Double Stacir 2*238/97 | 8 | [6 empty] | 502 | 504 | 0 | 0 | B_AHMM_NDMT_2 | NDAMITTA | A_HAMAM |  | محول تيار |  |  | 0.00094648 | 0.00558 | 0.01303 | 0.0046623 | 0.019474 | 0.0081159 | 0.012823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط | المحلة | DOMIAAT | MEHALA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 80 | 2000/1 | 1200/1 | 1020 | 388.6608 | 1200 | 0.0068099 | 0.049917 | 0.14404 | 0.018182 | 0.15702 | 0.086346 | 0.097521 | 3.296 | 24.16 | 0.0002976 | 8.8 | 76 | 0.0001784 | 47.2 | 2*380/50 ACSR | 80 | [6 empty] | 500 | 518 | 0 | 0 | B_DMTP_MHLA_1 | DEMITAPS | MEHALLA |  |  |  |  | 0.0068099 | 0.049917 | 0.14404 | 0.018182 | 0.15702 | 0.086346 | 0.097521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمياط | المحلة | DOMIAAT | MEHALA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 80 | 2000/1 | 1200/1 | 1020 | 388.6608 | 1200 | 0.0068099 | 0.049917 | 0.14404 | 0.018182 | 0.15702 | 0.086346 | 0.097521 | 3.296 | 24.16 | 0.0002976 | 8.8 | 76 | 0.0001784 | 47.2 | 2*380/50 ACSR | 80 | [6 empty] | 500 | 518 | 0 | 0 | B_DMTP_MHLA_2 | DEMITAPS | MEHALLA |  |  |  |  | 0.0068099 | 0.049917 | 0.14404 | 0.018182 | 0.15702 | 0.086346 | 0.097521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اولاد حمام | الجمالية | A.HAMAM | GAMALIA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 33 | 2000/1 | 2000/1 | 1020 | 388.6608 | 1200 | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 1.3596 | 9.966 | 0.00012276 | 3.63 | 31.35 | 7.359e-05 | 19.47 | 2*380/50 ACSR | 33 | [6 empty] | 504 | 506 | 0 | 0 | B_AHMM_GMLI_1 | A_HAMAM | GAMALIA |  | متهالك |  |  | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اولاد حمام | الجمالية | A.HAMAM | GAMALIA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 33 | 2000/1 | 2000/1 | 1020 | 388.6608 | 1200 | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 1.3596 | 9.966 | 0.00012276 | 3.63 | 31.35 | 7.359e-05 | 19.47 | 2*380/50 ACSR | 33 | [6 empty] | 504 | 506 | 0 | 0 | B_AHMM_GMLI_2 | A_HAMAM | GAMALIA |  | متهالك |  |  | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
تمي الامديد | سندوب | TIMY.AMDID | SANDOOB | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 23.4 | 2500/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0019919 | 0.014601 | 0.042131 | 0.0053182 | 0.04593 | 0.025256 | 0.028525 | 0.96408 | 7.0668 | 8.7048e-05 | 2.574 | 22.23 | 5.2182e-05 | 13.806 | 2*380/50 ACSR | 23.4 | [6 empty] | 501 | 511 | 0 | 0 | B_AMDED_SNDB_1 | T_AMADED | SANDOB |  | متهالك |  |  | 0.0019919 | 0.014601 | 0.042131 | 0.0053182 | 0.04593 | 0.025256 | 0.028525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
تمي الامديد | سندوب | TIMY.AMDID | SANDOOB | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 23.4 | 2500/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0019919 | 0.014601 | 0.042131 | 0.0053182 | 0.04593 | 0.025256 | 0.028525 | 0.96408 | 7.0668 | 8.7048e-05 | 2.574 | 22.23 | 5.2182e-05 | 13.806 | 2*380/50 ACSR | 23.4 | [6 empty] | 501 | 511 | 0 | 0 | B_AMDED_SNDB_2 | T_AMADED | SANDOB |  | متهالك |  |  | 0.0019919 | 0.014601 | 0.042131 | 0.0053182 | 0.04593 | 0.025256 | 0.028525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
تمي الامديد | الجمالية | TIMY.AMDID | GAMALIA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 58.9 | 2500/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0050138 | 0.036752 | 0.10605 | 0.013386 | 0.11561 | 0.063572 | 0.0718 | 2.4267 | 17.7878 | 0.00021911 | 6.479 | 55.955 | 0.00013135 | 34.751 | 2*380/50 ACSR | 58.9 | [6 empty] | 501 | 506 | 0 | 0 | B_GMLI_AMDED_1 | T_AMADED | GAMALIA |  | متهالك |  |  | 0.0050138 | 0.036752 | 0.10605 | 0.013386 | 0.11561 | 0.063572 | 0.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
تمي الامديد | الجمالية | TIMY.AMDID | GAMALIA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 58.9 | 2500/1 | 1200/1 | 800 | 304.832 | 1200 | 0.0050138 | 0.036752 | 0.10605 | 0.013386 | 0.11561 | 0.063572 | 0.0718 | 2.4267 | 17.7878 | 0.00021911 | 6.479 | 55.955 | 0.00013135 | 34.751 | 2*380/50 ACSR | 58.9 | [6 empty] | 501 | 506 | 0 | 0 | B_GMLI_AMDED_2 | T_AMADED | GAMALIA |  | متهالك |  |  | 0.0050138 | 0.036752 | 0.10605 | 0.013386 | 0.11561 | 0.063572 | 0.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحلة | سمنود | MEHALA | SAMANOD | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 31.5 | 1200/1 | 2500/1 | 1000 | 381.04 | 1200 | 0.0026814 | 0.019655 | 0.056715 | 0.0071591 | 0.061829 | 0.033999 | 0.038399 | 1.2978 | 9.513 | 0.00011718 | 3.465 | 29.925 | 7.0245e-05 | 18.585 | 2*380/50 ACSR | 31.5 | [6 empty] | 518 | 525 | 0 | 0 | B_MHLA_SMND_1 | MEHALLA | SMNOD500 |  |  |  |  | 0.0026814 | 0.019655 | 0.056715 | 0.0071591 | 0.061829 | 0.033999 | 0.038399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحلة | سمنود | MEHALA | SAMANOD | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 31.5 | 1200/1 | 2500/1 | 1000 | 381.04 | 1200 | 0.0026814 | 0.019655 | 0.056715 | 0.0071591 | 0.061829 | 0.033999 | 0.038399 | 1.2978 | 9.513 | 0.00011718 | 3.465 | 29.925 | 7.0245e-05 | 18.585 | 2*380/50 ACSR | 31.5 | [6 empty] | 518 | 525 | 0 | 0 | B_MHLA_SMND_2 | MEHALLA | SMNOD500 |  |  |  |  | 0.0026814 | 0.019655 | 0.056715 | 0.0071591 | 0.061829 | 0.033999 | 0.038399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | سمنود | TANTA | SAMANOD | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 18 | 1200/1 | 2500/1 | 1000 | 381.04 | 1200 | 0.0015322 | 0.011231 | 0.032409 | 0.0040909 | 0.035331 | 0.019428 | 0.021942 | 0.7416 | 5.436 | 6.696e-05 | 1.98 | 17.1 | 4.014e-05 | 10.62 | 2*380/50 ACSR | 18 | [6 empty] | 520 | 525 | 0 | 0 | B_SMND_TNTA_1 | TANTA | SMNOD500 |  |  |  |  | 0.0015322 | 0.011231 | 0.032409 | 0.0040909 | 0.035331 | 0.019428 | 0.021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | سمنود | TANTA | SAMANOD | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 18 | 1200/1 | 2500/1 | 1000 | 381.04 | 1200 | 0.0015322 | 0.011231 | 0.032409 | 0.0040909 | 0.035331 | 0.019428 | 0.021942 | 0.7416 | 5.436 | 6.696e-05 | 1.98 | 17.1 | 4.014e-05 | 10.62 | 2*380/50 ACSR | 18 | [6 empty] | 520 | 525 | 0 | 0 | B_SMND_TNTA_2 | TANTA | SMNOD500 |  |  |  |  | 0.0015322 | 0.011231 | 0.032409 | 0.0040909 | 0.035331 | 0.019428 | 0.021942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | قويسنا | TANTA | KEWESNA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 37 | 1200/1 | 1600/1 | 1020 | 388.6608 | 1200 | 0.0031496 | 0.023087 | 0.066618 | 0.0084091 | 0.072624 | 0.039935 | 0.045103 | 1.5244 | 11.174 | 0.00013764 | 4.07 | 35.15 | 8.251e-05 | 21.83 | 2*380/50 ACSR | 37 | [6 empty] | 520 | 522 | 0 | 0 | B_QSNA_TNTA_1 | TANTA | QUESNA |  |  |  |  | 0.0031496 | 0.023087 | 0.066618 | 0.0084091 | 0.072624 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | قويسنا | TANTA | KEWESNA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 37 | 1200/1 | 1600/1 | 1020 | 388.6608 | 1200 | 0.0031496 | 0.023087 | 0.066618 | 0.0084091 | 0.072624 | 0.039935 | 0.045103 | 1.5244 | 11.174 | 0.00013764 | 4.07 | 35.15 | 8.251e-05 | 21.83 | 2*380/50 ACSR | 37 | [6 empty] | 520 | 522 | 0 | 0 | B_QSNA_TNTA_2 | TANTA | QUESNA |  |  |  |  | 0.0031496 | 0.023087 | 0.066618 | 0.0084091 | 0.072624 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الشيخ الجديدة | سيدي سالم | K-SHEKH-NEW | SIDI-SALM | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 33 | 2500/1 | 1600/1 | 1150 | 438.196 | 1200 | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 1.3596 | 9.966 | 0.00012276 | 3.63 | 31.35 | 7.359e-05 | 19.47 | 2*380/50 ACSR | 33 | [6 empty] | 515 | 516 | 0 | 0 | B_NKSHK_SALM1 | N_KSHEKH | SEDISALM |  |  |  |  | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الشيخ الجديدة | سيدي سالم | K-SHEKH-NEW | SIDI-SALM | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 33 | 2500/1 | 1600/1 | 1150 | 438.196 | 1200 | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 1.3596 | 9.966 | 0.00012276 | 3.63 | 31.35 | 7.359e-05 | 19.47 | 2*380/50 ACSR | 33 | [6 empty] | 515 | 516 | 0 | 0 | B_NKSHK_SALM2 | N_KSHEKH | SEDISALM |  |  |  |  | 0.0028091 | 0.020591 | 0.059416 | 0.0075 | 0.064773 | 0.035618 | 0.040227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الشيخ القديمة | كفر الشيخ الجديدة | KAFR-SHEKH | K-SHEKH-NEW | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 10.825 | 1200/1 | 2500/1 | 1150 | 438.196 | 1200 | 0.00092147 | 0.0067544 | 0.01949 | 0.0024602 | 0.021247 | 0.011684 | 0.013196 | 0.44599 | 3.2691 | 4.0269e-05 | 1.1907 | 10.2837 | 2.414e-05 | 6.3867 | 2*380/50 ACSR | 10.825 | [6 empty] | 514 | 515 | 0 | 0 | B_KSHI_NKSHK_1 | KSHIEKH | N_KSHEKH |  |  |  |  | 0.00092147 | 0.0067544 | 0.01949 | 0.0024602 | 0.021247 | 0.011684 | 0.013196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الشيخ القديمة | كفر الشيخ الجديدة | KAFR-SHEKH | K-SHEKH-NEW | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 10.825 | 1200/1 | 2500/1 | 1150 | 438.196 | 1200 | 0.00092147 | 0.0067544 | 0.01949 | 0.0024602 | 0.021247 | 0.011684 | 0.013196 | 0.44599 | 3.2691 | 4.0269e-05 | 1.1907 | 10.2837 | 2.414e-05 | 6.3867 | 2*380/50 ACSR | 10.825 | [6 empty] | 514 | 515 | 0 | 0 | B_KSHI_NKSHK_2 | KSHIEKH | N_KSHEKH |  |  |  |  | 0.00092147 | 0.0067544 | 0.01949 | 0.0024602 | 0.021247 | 0.011684 | 0.013196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | كفر الزيات | TANTA | KAFR.ZYAIT | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 32 | 1200/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 1.3184 | 9.664 | 0.00011904 | 3.52 | 30.4 | 7.136e-05 | 18.88 | 2*380/50 ACSR | 32 | [6 empty] | 520 | 530 | 0 | 0 | B_KZ20_TNTA_1 | TANTA | KFZYT220 |  |  |  |  | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | كفر الزيات | TANTA | KAFR.ZYAIT | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 32 | 1200/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 1.3184 | 9.664 | 0.00011904 | 3.52 | 30.4 | 7.136e-05 | 18.88 | 2*380/50 ACSR | 32 | [6 empty] | 520 | 530 | 0 | 0 | B_KZ20_TNTA_2 | TANTA | KFZYT220 |  |  |  |  | 0.002724 | 0.019967 | 0.057615 | 0.0072727 | 0.06281 | 0.034538 | 0.039008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | توسيع ايتاي | KAFR.ZYAIT | ETY-BARD | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 30 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 1.236 | 9.06 | 0.0001116 | 3.3 | 28.5 | 6.69e-05 | 17.7 | 2*380/50 ACSR | 30 | [6 empty] | 530 | 612 | 0 | 0 | B_EBRD_KZ20_1 | KFZYT220 | ETAY500 |  |  |  |  | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | توسيع ايتاي | KAFR.ZYAIT | ETY-BARD | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 30 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 1.236 | 9.06 | 0.0001116 | 3.3 | 28.5 | 6.69e-05 | 17.7 | 2*380/50 ACSR | 30 | [6 empty] | 530 | 612 | 0 | 0 | B_EBRD_KZ20_2 | KFZYT220 | ETAY500 |  |  |  |  | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | توسيع ايتاي | ETY-BARD | ETY-BARD | وسط الدلتا | Circuit | 1 | 220 | 2*507 AAAC | 0.003 | 2000/1 | 1600/1 | 1250 | 476.3 | 1500 | 2.2934e-07 | 1.8471e-06 | 5.4595e-06 | 2.3554e-06 | 5.8884e-06 | 3.238e-06 | 3.657e-06 | 0.000111 | 0.000894 | 1.128e-08 | 0.00114 | 0.00285 | 6.69e-09 | 0.00177 | 2*507 AAAC | 0.003 | [6 empty] | 611 | 612 | 0 | 0 | B_ETAY1_ETAY2 | ETAYBARD | ETAY500 |  | مفتاح الخلية ناحية ايتاي القديمة لايتحمل اكثر من 1250 امبير |  |  | 2.2934e-07 | 1.8471e-06 | 5.4595e-06 | 2.3554e-06 | 5.8884e-06 | 3.238e-06 | 3.657e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزقازيق | سندوب | ZAGAZIG | SANDOOB | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 54 | 1500/1 | 1200/1 | 1080 | 411.5232 | 1200 | 0.0045967 | 0.033694 | 0.097226 | 0.012273 | 0.10599 | 0.058283 | 0.065826 | 2.2248 | 16.308 | 0.00020088 | 5.94 | 51.3 | 0.00012042 | 31.86 | 2*380/50 ACSR | 54 | [6 empty] | 370 | 511 | 0 | 0 | B_SNDOB_ZAGZ_1 | ZAGAZIG | SANDOB |  |  |  |  | 0.0045967 | 0.033694 | 0.097226 | 0.012273 | 0.10599 | 0.058283 | 0.065826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الزقازيق | سندوب | ZAGAZIG | SANDOOB | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 54 | 1500/1 | 1200/1 | 1080 | 411.5232 | 1200 | 0.0045967 | 0.033694 | 0.097226 | 0.012273 | 0.10599 | 0.058283 | 0.065826 | 2.2248 | 16.308 | 0.00020088 | 5.94 | 51.3 | 0.00012042 | 31.86 | 2*380/50 ACSR | 54 | [6 empty] | 370 | 511 | 0 | 0 | B_SNDOB_ZAGZ_2 | ZAGAZIG | SANDOB |  |  |  |  | 0.0045967 | 0.033694 | 0.097226 | 0.012273 | 0.10599 | 0.058283 | 0.065826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | القليوبية | BASSOS | KALUBIA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 21 | 3000/1 | 1200/1 | 1000 | 381.04 | 1200 | 0.0017876 | 0.013103 | 0.03781 | 0.0047727 | 0.041219 | 0.022666 | 0.025599 | 0.8652 | 6.342 | 7.812e-05 | 2.31 | 19.95 | 4.683e-05 | 12.39 | 2*380/50 ACSR | 21 | [6 empty] | 478 | 524 | 0 | 0 | B_BASS_KALB_1 | BASSOUS | KALYOBIA |  |  |  |  | 0.0017876 | 0.013103 | 0.03781 | 0.0047727 | 0.041219 | 0.022666 | 0.025599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | القليوبية | BASSOS | KALUBIA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 21 | 3000/1 | 1200/1 | 1000 | 381.04 | 1200 | 0.0017876 | 0.013103 | 0.03781 | 0.0047727 | 0.041219 | 0.022666 | 0.025599 | 0.8652 | 6.342 | 7.812e-05 | 2.31 | 19.95 | 4.683e-05 | 12.39 | 2*380/50 ACSR | 21 | [6 empty] | 478 | 524 | 0 | 0 | B_BASS_KALB_2 | BASSOUS | KALYOBIA |  |  |  |  | 0.0017876 | 0.013103 | 0.03781 | 0.0047727 | 0.041219 | 0.022666 | 0.025599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | توليد بنها | EST.BANHA | BANHA-GEN | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 6.5 | 1600/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.2678 | 1.963 | 2.418e-05 | 0.715 | 6.175 | 1.4495e-05 | 3.835 | 2*380/50 ACSR | 6.5 | [6 empty] | 521 | 523 | 0 | 0 | B_BNHE_BNHAG_1 | BANHAEST | BANHAPS |  |  |  |  | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | توليد بنها | EST.BANHA | BANHA-GEN | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 6.5 | 1600/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.2678 | 1.963 | 2.418e-05 | 0.715 | 6.175 | 1.4495e-05 | 3.835 | 2*380/50 ACSR | 6.5 | [6 empty] | 521 | 523 | 0 | 0 | B_BNHE_BNHAG_2 | BANHAEST | BANHAPS |  |  |  |  | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | القليوبية | EST.BANHA | KALUBIA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 27 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 1.1124 | 8.154 | 0.00010044 | 2.97 | 25.65 | 6.021e-05 | 15.93 | 2*380/50 ACSR | 27 | [6 empty] | 521 | 524 | 0 | 0 | B_BNHAE_KALB_1 | BANHAEST | KALYOBIA |  |  |  |  | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق بنها | القليوبية | EST.BANHA | KALUBIA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 27 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 1.1124 | 8.154 | 0.00010044 | 2.97 | 25.65 | 6.021e-05 | 15.93 | 2*380/50 ACSR | 27 | [6 empty] | 521 | 524 | 0 | 0 | B_BNHAE_KALB_2 | BANHAEST | KALYOBIA |  |  |  |  | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
قويسنا | توليد بنها | KEWESNA | BANHA-GEN | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 18.5 | 1600/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.0015748 | 0.011543 | 0.033309 | 0.0042045 | 0.036312 | 0.019967 | 0.022552 | 0.7622 | 5.587 | 6.882e-05 | 2.035 | 17.575 | 4.1255e-05 | 10.915 | 2*380/50 ACSR | 18.5 | [6 empty] | 522 | 523 | 0 | 0 | B_BNHA_QSNA_1 | QUESNA | BANHAPS |  |  |  |  | 0.0015748 | 0.011543 | 0.033309 | 0.0042045 | 0.036312 | 0.019967 | 0.022552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
قويسنا | توليد بنها | KEWESNA | BANHA-GEN | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 18.5 | 1600/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.0015748 | 0.011543 | 0.033309 | 0.0042045 | 0.036312 | 0.019967 | 0.022552 | 0.7622 | 5.587 | 6.882e-05 | 2.035 | 17.575 | 4.1255e-05 | 10.915 | 2*380/50 ACSR | 18.5 | [6 empty] | 522 | 523 | 0 | 0 | B_BNHA_QSNA_2 | QUESNA | BANHAPS |  |  |  |  | 0.0015748 | 0.011543 | 0.033309 | 0.0042045 | 0.036312 | 0.019967 | 0.022552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القليوبية | اشمون | KALUBIA | ASHMOON | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 26 | 1200/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.0022132 | 0.016223 | 0.046812 | 0.0059091 | 0.051033 | 0.028062 | 0.031694 | 1.0712 | 7.852 | 9.672e-05 | 2.86 | 24.7 | 5.798e-05 | 15.34 | 2*380/50 ACSR | 26 | [6 empty] | 524 | 528 | 0 | 0 | B_ASHMN_KALB_1 | KALYOBIA | ASHMON |  |  |  |  | 0.0022132 | 0.016223 | 0.046812 | 0.0059091 | 0.051033 | 0.028062 | 0.031694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القليوبية | اشمون | KALUBIA | ASHMOON | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 26 | 800/1 | 1600/1 | 800 | 304.832 | 1200 | 0.0022132 | 0.016223 | 0.046812 | 0.0059091 | 0.051033 | 0.028062 | 0.031694 | 1.0712 | 7.852 | 9.672e-05 | 2.86 | 24.7 | 5.798e-05 | 15.34 | 2*380/50 ACSR | 26 | [6 empty] | 524 | 528 | 0 | 0 | B_ASHM_KALB_2 | KALYOBIA | ASHMON |  | محولات التيار |  |  | 0.0022132 | 0.016223 | 0.046812 | 0.0059091 | 0.051033 | 0.028062 | 0.031694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | اشمون | MENOUF | ASHMOON | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 25 | 800/1 | 1600/1 | 800 | 304.832 | 1200 | 0.0021281 | 0.015599 | 0.045012 | 0.0056818 | 0.04907 | 0.026983 | 0.030475 | 1.03 | 7.55 | 9.3e-05 | 2.75 | 23.75 | 5.575e-05 | 14.75 | 2*380/50 ACSR | 25 | [6 empty] | 526 | 528 | 0 | 0 | B_ASHM_MNOF_1 | MENOUF | ASHMON |  | محولات التيار |  |  | 0.0021281 | 0.015599 | 0.045012 | 0.0056818 | 0.04907 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | اشمون | MENOUF | ASHMOON | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 25 | 800/1 | 1600/1 | 800 | 304.832 | 1200 | 0.0021281 | 0.015599 | 0.045012 | 0.0056818 | 0.04907 | 0.026983 | 0.030475 | 1.03 | 7.55 | 9.3e-05 | 2.75 | 23.75 | 5.575e-05 | 14.75 | 2*380/50 ACSR | 25 | [6 empty] | 526 | 528 | 0 | 0 | B_ASHM_MNOF_2 | MENOUF | ASHMON |  | محولات التيار |  |  | 0.0021281 | 0.015599 | 0.045012 | 0.0056818 | 0.04907 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | منوف | BASSOS | MENOUF | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR 1*380/88 ACSR | 75 | 3000/1 | 800/1 | 650 | 247.676 | 650 | 0.01141 | 0.05844 | 0.11082 | 0.039618 | 0.14721 | 0.080949 | 0.091426 | 5.5223 | 28.285 | 0.00022898 | 19.175 | 71.25 | 0.00016725 | 44.25 | 2*380/50 ACSR | 17.5 | 1*380/88 ACSR | 57.5 |  |  |  |  | 478 | 526 | 0 | 0 | B_BASS_MNOF_1 | BASSOUS | MENOUF |  |  |  |  | 0.0014897 | 0.010919 | 0.031508 | 0.0039773 | 0.034349 | 0.018888 | 0.021333 | 0.0099199 | 0.047521 | 0.079315 | 0.03564 | 0.11286 | 0.062061 | 0.070093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
باسوس | منوف | BASSOS | MENOUF | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR 1*380/88 ACSR | 75 | 3000/1 | 800/1 | 650 | 247.676 | 650 | 0.01141 | 0.05844 | 0.11082 | 0.039618 | 0.14721 | 0.080949 | 0.091426 | 5.5223 | 28.285 | 0.00022898 | 19.175 | 71.25 | 0.00016725 | 44.25 | 2*380/50 ACSR | 17.5 | 1*380/88 ACSR | 57.5 |  |  |  |  | 478 | 526 | 0 | 0 | B_BASS_MNOF_2 | BASSOUS | MENOUF |  |  |  |  | 0.0014897 | 0.010919 | 0.031508 | 0.0039773 | 0.034349 | 0.018888 | 0.021333 | 0.0099199 | 0.047521 | 0.079315 | 0.03564 | 0.11286 | 0.062061 | 0.070093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحلة | المحمودية الجديدة | MEHALA | N.MHMODIA | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 86 | 1200/1 | 2000/1 | 1100 | 419.144 | 1200 | 0.0073207 | 0.053661 | 0.15484 | 0.019545 | 0.1688 | 0.092822 | 0.10483 | 3.5432 | 25.972 | 0.00031992 | 9.46 | 81.7 | 0.00019178 | 50.74 | 2*380/50 ACSR | 86 | [6 empty] | 518 | 602 | 0 | 0 | B_MHLA_NMHMD_1 | MEHALLA | NMHMODIA |  |  |  |  | 0.0073207 | 0.053661 | 0.15484 | 0.019545 | 0.1688 | 0.092822 | 0.10483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحلة | المحمودية الجديدة | MEHALA | N.MHMODIA | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 86 | 1200/1 | 2000/1 | 1100 | 419.144 | 1200 | 0.0073207 | 0.053661 | 0.15484 | 0.019545 | 0.1688 | 0.092822 | 0.10483 | 3.5432 | 25.972 | 0.00031992 | 9.46 | 81.7 | 0.00019178 | 50.74 | 2*380/50 ACSR | 86 | [6 empty] | 518 | 602 | 0 | 0 | B_MHLA_NMHMD_2 | MEHALLA | NMHMODIA |  |  |  |  | 0.0073207 | 0.053661 | 0.15484 | 0.019545 | 0.1688 | 0.092822 | 0.10483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | اشمون | NRTH-GIZA | ASHMOON | وسط الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 9.3 | 2000/1 | 1600/1 | 1150 | 438.196 | 1200 | 0.00079165 | 0.0058029 | 0.016744 | 0.0021136 | 0.018254 | 0.010038 | 0.011337 | 0.38316 | 2.8086 | 3.4596e-05 | 1.023 | 8.835 | 2.0739e-05 | 5.487 | 2*380/50 ACSR | 9.3 | [6 empty] | 401 | 529 | 0 | 0 | B_ASHM_GIZAN_1 | GIZANRTH | ASHMON |  |  |  |  | 0.00079165 | 0.0058029 | 0.016744 | 0.0021136 | 0.018254 | 0.010038 | 0.011337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | اشمون | NRTH-GIZA | ASHMOON | وسط الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 9.3 | 2000/1 | 1600/1 | 1150 | 438.196 | 1200 | 0.00079165 | 0.0058029 | 0.016744 | 0.0021136 | 0.018254 | 0.010038 | 0.011337 | 0.38316 | 2.8086 | 3.4596e-05 | 1.023 | 8.835 | 2.0739e-05 | 5.487 | 2*380/50 ACSR | 9.3 | [6 empty] | 401 | 529 | 0 | 0 | B_ASHM_GIZAN_2 | GIZANRTH | ASHMON |  |  |  |  | 0.00079165 | 0.0058029 | 0.016744 | 0.0021136 | 0.018254 | 0.010038 | 0.011337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب دمياط | توسيع غرب دمياط | W.DOMIAT | N.W.DOM-GEN | وسط الدلتا | Circuit | 1 | 220 | Thermal Double Stacir 2*238/97 | 1 | 2000/1 | 2000/1 | 1500 | 571.56 | 2400 | 0.00011831 | 0.0006975 | 0.0016287 | 0.00058279 | 0.0024343 | 0.0010145 | 0.0016029 | 0.057262 | 0.33759 | 3.3651e-06 | 0.28207 | 1.1782 | 2.096e-06 | 0.77578 | Thermal Double Stacir 2*238/97 | 1 | [6 empty] | 507 | 508 | 0 | 0 | B_WDMT2_WDMT_1 | WDAMITTA | WDMTTA_2 |  | يوجد كابل 1*1200 بين الخلية و الدائرة وهي تتحمل 1050 امبير ولكن افادت الوردية ان السعة المتاحة 1500 امبير |  |  | 0.00011831 | 0.0006975 | 0.0016287 | 0.00058279 | 0.0024343 | 0.0010145 | 0.0016029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب دمياط | توسيع غرب دمياط | W.DOMIAT | N.W.DOM-GEN | وسط الدلتا | Circuit | 2 | 220 | Thermal Double Stacir 2*238/97 | 1 | 2000/1 | 2000/1 | 1500 | 571.56 | 2400 | 0.00011831 | 0.0006975 | 0.0016287 | 0.00058279 | 0.0024343 | 0.0010145 | 0.0016029 | 0.057262 | 0.33759 | 3.3651e-06 | 0.28207 | 1.1782 | 2.096e-06 | 0.77578 | Thermal Double Stacir 2*238/97 | 1 | [6 empty] | 507 | 508 | 0 | 0 | B_WDMT2_WDMT_2 | WDAMITTA | WDMTTA_2 |  | يوجد كابل 1*1200 بين الخلية و الدائرة وهي تتحمل 1050 امبير ولكن افادت الوردية ان السعة المتاحة 1500 امبير |  |  | 0.00011831 | 0.0006975 | 0.0016287 | 0.00058279 | 0.0024343 | 0.0010145 | 0.0016029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الدوار | العامرية | KAFR-DAWAR | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*375.2/87 MCM 740 | 37.5 | 1200/1 | 1500/1 | 1200 | 457.248 | 1200 | 0.0057218 | 0.046077 | 0.13504 | 0.058264 | 0.14566 | 0.080132 | 0.090496 | 2.7694 | 22.3012 | 0.000279 | 28.2 | 70.5 | 0.00016556 | 43.8 | 1*375.2/87 MCM 740 | 37.5 | [6 empty] | 608 | 668 | 0 | 0 | B_AMRI_KDWR_1 | KDAWAR | AMRIA |  |  |  |  | 0.0057218 | 0.046077 | 0.13504 | 0.058264 | 0.14566 | 0.080132 | 0.090496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الدوار | العامرية | KAFR-DAWAR | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*375.2/87 MCM 740 | 37.5 | 1200/1 | 1500/1 | 1200 | 457.248 | 1200 | 0.0057218 | 0.046077 | 0.13504 | 0.058264 | 0.14566 | 0.080132 | 0.090496 | 2.7694 | 22.3012 | 0.000279 | 28.2 | 70.5 | 0.00016556 | 43.8 | 1*375.2/87 MCM 740 | 37.5 | [6 empty] | 608 | 668 | 0 | 0 | B_AMRI_KDWR_2 | KDAWAR | AMRIA |  |  |  |  | 0.0057218 | 0.046077 | 0.13504 | 0.058264 | 0.14566 | 0.080132 | 0.090496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALEX WEST | سيدي كرير | ALEX WEST | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 11.2 | 2500/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0010629 | 0.0067397 | 0.057327 | 0.0030671 | 0.017409 | 0.045641 | 0.01219 | 0.51444 | 3.262 | 0.00011844 | 1.4845 | 8.426 | 9.43e-05 | 5.9 | 2*405 AAAC | 10 | XLPE 2000mm2 Elswedy | 1.2 | [6 empty] | 0 | 0 | B_WALEX_KRIR1 | ALEX_WST | SIDIKRER |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 3.1909e-05 | 0.0004174 | 0.041597 | 0.00038117 | 0.00026028 | 0.034848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALEX WEST | سيدي كرير | ALEX WEST | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit & Cable | 2 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 11.2 | 2500/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0010629 | 0.0067397 | 0.057327 | 0.0030671 | 0.017409 | 0.045641 | 0.01219 | 0.51444 | 3.262 | 0.00011844 | 1.4845 | 8.426 | 9.43e-05 | 5.9 | 2*405 AAAC | 10 | XLPE 2000mm2 Elswedy | 1.2 | [6 empty] | 0 | 0 | B_WALEX_KRIR2 | ALEX_WST | SIDIKRER |  |  |  |  | 0.001031 | 0.0063223 | 0.01573 | 0.002686 | 0.017149 | 0.010793 | 0.01219 | 3.1909e-05 | 0.0004174 | 0.041597 | 0.00038117 | 0.00026028 | 0.034848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العامرية | ALEX WEST | AMEREIA | ALEX WEST | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 15.2 | 1500/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0014753 | 0.0092686 | 0.063619 | 0.0041415 | 0.024269 | 0.049958 | 0.017066 | 0.71404 | 4.486 | 0.00013144 | 2.0045 | 11.746 | 0.00010322 | 8.26 | 2*405 AAAC | 14 | XLPE 2000mm2 Elswedy | 1.2 | [6 empty] | 0 | 0 | B_AMRI_WALEX_1 | AMRIA | ALEX_WST |  |  |  |  | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 3.1909e-05 | 0.0004174 | 0.041597 | 0.00038117 | 0.00026028 | 0.034848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العامرية | ALEX WEST | AMEREIA | ALEX WEST | الاسكندرية وغرب الدلتا | Circuit & Cable | 2 | 220 | 2*405 AAAC XLPE 2000mm2 Elswedy | 15.2 | 1500/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0014753 | 0.0092686 | 0.063619 | 0.0041415 | 0.024269 | 0.049958 | 0.017066 | 0.71404 | 4.486 | 0.00013144 | 2.0045 | 11.746 | 0.00010322 | 8.26 | 2*405 AAAC | 14 | XLPE 2000mm2 Elswedy | 1.2 | [6 empty] | 0 | 0 | B_AMRI_WALEX_2 | AMRIA | ALEX_WST |  |  |  |  | 0.0014434 | 0.0088512 | 0.022022 | 0.0037603 | 0.024008 | 0.01511 | 0.017066 | 3.1909e-05 | 0.0004174 | 0.041597 | 0.00038117 | 0.00026028 | 0.034848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغزل | العامرية | GHAZL | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 5.72 | 1500/1 | 1500/1 | 1150 | 438.196 | 1150 | 0.00058973 | 0.0036164 | 0.0089976 | 0.0015364 | 0.0098091 | 0.0061737 | 0.0069727 | 0.28543 | 1.7503 | 1.859e-05 | 0.7436 | 4.7476 | 1.2756e-05 | 3.3748 | 2*405 AAAC | 5.72 | [6 empty] | 652 | 668 | 0 | 0 | B_AMRI_TXTL_1 | TEXTILE | AMRIA |  |  |  |  | 0.00058973 | 0.0036164 | 0.0089976 | 0.0015364 | 0.0098091 | 0.0061737 | 0.0069727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الغزل | العامرية | GHAZL | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 5.72 | 1500/1 | 1500/1 | 1150 | 438.196 | 1150 | 0.00058973 | 0.0036164 | 0.0089976 | 0.0015364 | 0.0098091 | 0.0061737 | 0.0069727 | 0.28543 | 1.7503 | 1.859e-05 | 0.7436 | 4.7476 | 1.2756e-05 | 3.3748 | 2*405 AAAC | 5.72 | [6 empty] | 652 | 668 | 0 | 0 | B_AMRI_TXTL_2 | TEXTILE | AMRIA |  |  |  |  | 0.00058973 | 0.0036164 | 0.0089976 | 0.0015364 | 0.0098091 | 0.0061737 | 0.0069727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العامرية | الاثيلين | AMEREIA | ETHELIN | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*380/88 ACSR 1*405 AAAC | 9.5 | 750/1 | 1600/1 | 520 | 198.1408 | 650 | 0.0016379 | 0.0078698 | 0.013073 | 0.0058884 | 0.018647 | 0.010254 | 0.011581 | 0.79275 | 3.809 | 2.701e-05 | 2.85 | 9.025 | 2.1185e-05 | 5.605 | 1*380/88 ACSR | 9 | 1*405 AAAC | 0.5 |  |  |  |  | 668 | 677 | 0 | 0 | B_AMRI_ETHL_1 | AMRIA | ETHYLENE |  |  |  |  | 0.0015527 | 0.007438 | 0.012415 | 0.0055785 | 0.017665 | 0.0097139 | 0.010971 | 8.5227e-05 | 0.00043182 | 0.00065824 | 0.00030992 | 0.0009814 | 0.00053966 | 0.0006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العامرية | الاثيلين | AMEREIA | ETHELIN | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*380/88 ACSR 1*405 AAAC | 9.5 | 750/1 | 1600/1 | 520 | 198.1408 | 650 | 0.0016379 | 0.0078698 | 0.013073 | 0.0058884 | 0.018647 | 0.010254 | 0.011581 | 0.79275 | 3.809 | 2.701e-05 | 2.85 | 9.025 | 2.1185e-05 | 5.605 | 1*380/88 ACSR | 9 | 1*405 AAAC | 0.5 |  |  |  |  | 668 | 677 | 0 | 0 | B_AMRI_ETHL_2 | AMRIA | ETHYLENE |  |  |  |  | 0.0015527 | 0.007438 | 0.012415 | 0.0055785 | 0.017665 | 0.0097139 | 0.010971 | 8.5227e-05 | 0.00043182 | 0.00065824 | 0.00030992 | 0.0009814 | 0.00053966 | 0.0006095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنطقة الحرة | الاثيلين | FREE.ZON | ETHELIN | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*380/88 ACSR 1*405 AAAC | 20.6 | 600/1 | 1600/1 | 520 | 198.1408 | 650 | 0.0035353 | 0.01736 | 0.027849 | 0.012769 | 0.040434 | 0.022234 | 0.025112 | 1.7111 | 8.402 | 5.754e-05 | 6.18 | 19.57 | 4.5938e-05 | 12.154 | 1*380/88 ACSR | 11.6 | 1*405 AAAC | 9 |  |  |  |  | 676 | 677 | 0 | 0 | B_ETHL_FRZ1 | FREEZONE | ETHYLENE |  |  |  |  | 0.0020012 | 0.0095868 | 0.016001 | 0.0071901 | 0.022769 | 0.01252 | 0.01414 | 0.0015341 | 0.0077727 | 0.011848 | 0.0055785 | 0.017665 | 0.0097139 | 0.010971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنطقة الحرة | الاثيلين | FREE.ZON | ETHELIN | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*380/88 ACSR 1*405 AAAC | 20.6 | 600/1 | 1600/1 | 520 | 198.1408 | 650 | 0.0035353 | 0.01736 | 0.027849 | 0.012769 | 0.040434 | 0.022234 | 0.025112 | 1.7111 | 8.402 | 5.754e-05 | 6.18 | 19.57 | 4.5938e-05 | 12.154 | 1*380/88 ACSR | 11.6 | 1*405 AAAC | 9 |  |  |  |  | 676 | 677 | 0 | 0 | B_ETHL_FRZ2 | FREEZONE | ETHYLENE |  |  |  |  | 0.0020012 | 0.0095868 | 0.016001 | 0.0071901 | 0.022769 | 0.01252 | 0.01414 | 0.0015341 | 0.0077727 | 0.011848 | 0.0055785 | 0.017665 | 0.0097139 | 0.010971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | العامرية | DEKHELA | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 5.8 | 800/1 | 750/1 | 1000 | 381.04 | 1150 | 0.00059798 | 0.0036669 | 0.0091234 | 0.0015579 | 0.0099463 | 0.0062601 | 0.0070702 | 0.28942 | 1.7748 | 1.885e-05 | 0.754 | 4.814 | 1.2934e-05 | 3.422 | 2*405 AAAC | 5.8 | [6 empty] | 664 | 668 | 0 | 0 | B_AMRI_DEKH_1 | DEKHELA | AMRIA |  |  |  |  | 0.00059798 | 0.0036669 | 0.0091234 | 0.0015579 | 0.0099463 | 0.0062601 | 0.0070702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | العامرية | DEKHELA | AMEREIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 5.8 | 800/1 | 750/1 | 1000 | 381.04 | 1150 | 0.00059798 | 0.0036669 | 0.0091234 | 0.0015579 | 0.0099463 | 0.0062601 | 0.0070702 | 0.28942 | 1.7748 | 1.885e-05 | 0.754 | 4.814 | 1.2934e-05 | 3.422 | 2*405 AAAC | 5.8 | [6 empty] | 664 | 668 | 0 | 0 | B_AMRI_DEKH_2 | DEKHELA | AMRIA |  |  |  |  | 0.00059798 | 0.0036669 | 0.0091234 | 0.0015579 | 0.0099463 | 0.0062601 | 0.0070702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنطقة الحرة | سوميد | FREE.ZON | SOMID | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 1*380/88 ACSR XLPE 1*400 cable 1*405 AAAC | 9.8 | 600/1 | 400/1 | 300 | 114.312 | 300 | 0.0016104 | 0.0082441 | 0.026776 | 0.0059429 | 0.018331 | 0.022138 | 0.011337 | 0.77945 | 3.9901 | 5.5322e-05 | 2.8763 | 8.8722 | 4.5739e-05 | 5.487 | 1*380/88 ACSR | 4.65 | XLPE 1*400 cable | 0.5 | 1*405 AAAC | 4.65 |  |  | 676 | 678 | 0 | 0 | B_FZON_SOMD_1 | FREEZONE | SOMID |  |  |  |  | 0.00080222 | 0.003843 | 0.0064142 | 0.0028822 | 0.0091271 | 0.0050188 | 0.0056684 | 1.5599e-05 | 0.00038523 | 0.01424 | 0.00017841 | 7.6756e-05 | 0.0121 | 0 | 0.00079261 | 0.0040159 | 0.0061216 | 0.0028822 | 0.0091271 | 0.0050188 | 0.0056684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنطقة الحرة | سوميد | FREE.ZON | SOMID | الاسكندرية وغرب الدلتا | Circuit & Cable | 2 | 220 | 1*380/88 ACSR XLPE 1*400 cable 1*405 AAAC | 9.8 | 600/1 | 400/1 | 300 | 114.312 | 300 | 0.0016104 | 0.0082441 | 0.026776 | 0.0059429 | 0.018331 | 0.022138 | 0.011337 | 0.77945 | 3.9901 | 5.5322e-05 | 2.8763 | 8.8722 | 4.5739e-05 | 5.487 | 1*380/88 ACSR | 4.65 | XLPE 1*400 cable | 0.5 | 1*405 AAAC | 4.65 |  |  | 676 | 678 | 0 | 0 | B_FZON_SOMD_2 | FREEZONE | SOMID |  |  |  |  | 0.00080222 | 0.003843 | 0.0064142 | 0.0028822 | 0.0091271 | 0.0050188 | 0.0056684 | 1.5599e-05 | 0.00038523 | 0.01424 | 0.00017841 | 7.6756e-05 | 0.0121 | 0 | 0.00079261 | 0.0040159 | 0.0061216 | 0.0028822 | 0.0091271 | 0.0050188 | 0.0056684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
برج العرب | المنطقة الحرة | BRG-ARB | FREE.ZON | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 33.4 | 1200/1 | 1200/1 | 1000 | 381.04 | 1150 | 0.0034435 | 0.021117 | 0.052538 | 0.0089711 | 0.057277 | 0.036049 | 0.040715 | 1.6667 | 10.2204 | 0.00010855 | 4.342 | 27.722 | 7.4482e-05 | 19.706 | 2*405 AAAC | 33.4 | [6 empty] | 674 | 676 | 0 | 0 | B_BARB_FZON_1 | BORGARB | FREEZONE |  | تقادم |  |  | 0.0034435 | 0.021117 | 0.052538 | 0.0089711 | 0.057277 | 0.036049 | 0.040715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
برج العرب | المنطقة الحرة | BRG-ARB | FREE.ZON | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 33.4 | 1200/1 | 1200/1 | 1000 | 381.04 | 1150 | 0.0034435 | 0.021117 | 0.052538 | 0.0089711 | 0.057277 | 0.036049 | 0.040715 | 1.6667 | 10.2204 | 0.00010855 | 4.342 | 27.722 | 7.4482e-05 | 19.706 | 2*405 AAAC | 33.4 | [6 empty] | 674 | 676 | 0 | 0 | B_BARB_FZON_2 | BORGARB | FREEZONE |  | تقادم |  |  | 0.0034435 | 0.021117 | 0.052538 | 0.0089711 | 0.057277 | 0.036049 | 0.040715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
برج العرب | العميد | BRG-ARB | OMAID | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 37 | 1200/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 1.8463 | 11.322 | 0.00012025 | 4.81 | 30.71 | 8.251e-05 | 21.83 | 2*405 AAAC | 37 | [6 empty] | 674 | 680 | 0 | 0 | B_BARB_OMID_1 | BORGARB | OMAID |  | تم الاتصال بمحطة العميد يوم 16_6_2021 والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
برج العرب | العميد | BRG-ARB | OMAID | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 37 | 1200/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 1.8463 | 11.322 | 0.00012025 | 4.81 | 30.71 | 8.251e-05 | 21.83 | 2*405 AAAC | 37 | [6 empty] | 674 | 680 | 0 | 0 | B_BARB_OMID_2 | BORGARB | OMAID |  | تم الاتصال بمحطة العميد يوم 16_6_2021 والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العميد | العلمين | OMAID | ALAMIN | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 40.2 | 1600/1 | 1250/1 | 1150 | 438.196 | 1150 | 0.0041446 | 0.025416 | 0.063235 | 0.010798 | 0.068938 | 0.043389 | 0.049004 | 2.006 | 12.3012 | 0.00013065 | 5.226 | 33.366 | 8.9646e-05 | 23.718 | 2*405 AAAC | 40.2 | [6 empty] | 680 | 685 | 0 | 0 |  | OMAID | EL_ALMEN |  | تم الاتصال بمحطة العميد يوم 16_6_2021 والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0041446 | 0.025416 | 0.063235 | 0.010798 | 0.068938 | 0.043389 | 0.049004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العميد | العلمين | OMAID | ALAMIN | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 40.2 | 1600/1 | 1250/1 | 1150 | 438.196 | 1150 | 0.0041446 | 0.025416 | 0.063235 | 0.010798 | 0.068938 | 0.043389 | 0.049004 | 2.006 | 12.3012 | 0.00013065 | 5.226 | 33.366 | 8.9646e-05 | 23.718 | 2*405 AAAC | 40.2 | [6 empty] | 680 | 685 | 0 | 0 |  | OMAID | EL_ALMEN |  | تم الاتصال بمحطة العميد يوم 16_6_2021 والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0041446 | 0.025416 | 0.063235 | 0.010798 | 0.068938 | 0.043389 | 0.049004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مراسي | العلمين | MARASI | ALAMIN | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 25.3 | 1600/1 | 1250/1 | 1150 | 438.196 | 1150 | 0.0026084 | 0.015995 | 0.039797 | 0.0067955 | 0.043386 | 0.027307 | 0.030841 | 1.2625 | 7.7418 | 8.2225e-05 | 3.289 | 20.999 | 5.6419e-05 | 14.927 | 2*405 AAAC | 25.3 | [6 empty] | 683 | 685 | 0 | 0 |  | MARASY | EL_ALMEN |  |  |  |  | 0.0026084 | 0.015995 | 0.039797 | 0.0067955 | 0.043386 | 0.027307 | 0.030841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مراسي | العلمين | MARASI | ALAMIN | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 25.3 | 1600/1 | 1250/1 | 1150 | 438.196 | 1150 | 0.0026084 | 0.015995 | 0.039797 | 0.0067955 | 0.043386 | 0.027307 | 0.030841 | 1.2625 | 7.7418 | 8.2225e-05 | 3.289 | 20.999 | 5.6419e-05 | 14.927 | 2*405 AAAC | 25.3 | [6 empty] | 683 | 685 | 0 | 0 |  | MARASY | EL_ALMEN |  | هذه الدائرة عليها متنقلة الحمرا على بعد 4.5 كم من محطة مراسي على دائرة مراسي / العلمين |  |  | 0.0026084 | 0.015995 | 0.039797 | 0.0067955 | 0.043386 | 0.027307 | 0.030841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الضبعة | مطروح | DABAA | MATROUH | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 135 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.013918 | 0.085351 | 0.21236 | 0.03626 | 0.23151 | 0.14571 | 0.16457 | 6.7365 | 41.31 | 0.00043875 | 17.55 | 112.05 | 0.00030105 | 79.65 | 2*405 AAAC | 135 | [6 empty] | 681 | 682 | 0 | 0 |  | DABAA | MATROHSS |  |  |  |  | 0.013918 | 0.085351 | 0.21235 | 0.03626 | 0.23151 | 0.14571 | 0.16457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الضبعة | مطروح | DABAA | MATROUH | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 135 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.013918 | 0.085351 | 0.21236 | 0.03626 | 0.23151 | 0.14571 | 0.16457 | 6.7365 | 41.31 | 0.00043875 | 17.55 | 112.05 | 0.00030105 | 79.65 | 2*405 AAAC | 135 | [6 empty] | 681 | 682 | 0 | 0 |  | DABAA | MATROHSS |  |  |  |  | 0.013918 | 0.085351 | 0.21235 | 0.03626 | 0.23151 | 0.14571 | 0.16457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الضبعة | مطروح | DABAA | MATROUH | الاسكندرية وغرب الدلتا | Circuit | 3 | 220 | 4*506 AAAC 2*405 AAAC | 140 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0054014 | 0.080398 | 0.28274 | 0.047077 | 0.25152 | 0.17863 | 0.063048 | 2.6143 | 38.9125 | 0.00058417 | 22.7852 | 121.7355 | 0.00036907 | 30.5152 | 4*506 AAAC | 133 | 2*405 AAAC | 7 |  |  |  |  | 681 | 682 | 0 | 0 |  | DABAA | MATROHSS |  |  |  |  | 0.0046797 | 0.075972 | 0.27173 | 0.045197 | 0.23952 | 0.17107 | 0.054515 | 0.00072169 | 0.0044256 | 0.011011 | 0.0018802 | 0.012004 | 0.0075552 | 0.0085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الترفيهية | الضبعة | BRGARBTRFHA | DABAA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 4*506 AAAC 2*405 AAAC | 132 | 1600/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0051199 | 0.075828 | 0.26639 | 0.044358 | 0.23711 | 0.16834 | 0.059769 | 2.4781 | 36.7007 | 0.0005504 | 21.4694 | 114.7625 | 0.00034781 | 28.9281 | 4*506 AAAC | 125 | 2*405 AAAC | 7 |  |  |  |  | 675 | 681 | 0 | 0 |  | TARFIHIA | DABAA |  |  |  |  | 0.0043982 | 0.071402 | 0.25538 | 0.042478 | 0.22511 | 0.16078 | 0.051236 | 0.00072169 | 0.0044256 | 0.011011 | 0.0018802 | 0.012004 | 0.0075552 | 0.0085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الترفيهية | مطروح | BRGARBTRFHA | MATROUH | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 4*506 AAAC | 258 | 1600/1 | 1600/1 | 1600 | 609.664 | 2600 | 0.009078 | 0.14737 | 0.52711 | 0.087675 | 0.46462 | 0.33186 | 0.10575 | 4.3937 | 71.3293 | 0.0010891 | 42.4346 | 224.878 | 0.00068566 | 51.1833 | 4*506 AAAC | 258 | [6 empty] | 675 | 682 | 0 | 0 | B_MMSS_TRFH_1 | TARFIHIA | MATROHSS |  | الخط اصلا جهده 500 ك ف ولكن تم وضع الجهد عليه ك 220 ك ف |  |  | 0.009078 | 0.14737 | 0.52711 | 0.087675 | 0.46462 | 0.33186 | 0.10575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الضبعة | مراسي | DABAA | MARASI | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 30 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.003093 | 0.018967 | 0.04719 | 0.0080579 | 0.051446 | 0.03238 | 0.03657 | 1.497 | 9.18 | 9.75e-05 | 3.9 | 24.9 | 6.69e-05 | 17.7 | 2*405 AAAC | 30 | [6 empty] | 681 | 683 | 0 | 0 |  | DABAA | MARASY |  |  |  |  | 0.003093 | 0.018967 | 0.04719 | 0.0080579 | 0.051446 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الضبعة | مراسي | DABAA | MARASI | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 30 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.003093 | 0.018967 | 0.04719 | 0.0080579 | 0.051446 | 0.03238 | 0.03657 | 1.497 | 9.18 | 9.75e-05 | 3.9 | 24.9 | 6.69e-05 | 17.7 | 2*405 AAAC | 30 | [6 empty] | 681 | 683 | 0 | 0 |  | DABAA | MARASY |  | تم الغاء متنقلة الضبعة |  |  | 0.003093 | 0.018967 | 0.04719 | 0.0080579 | 0.051446 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
أبو قير | ابيس | ABO.KIR | ABIS | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*454 AAAC | 26 | 600/1 | 800/1 | 600 | 228.624 | 700 | 0.0039 | 0.021488 | 0.034228 | 0.016116 | 0.051033 | 0.028062 | 0.031694 | 1.8876 | 10.4 | 7.072e-05 | 7.8 | 24.7 | 5.798e-05 | 15.34 | 1*454 AAAC | 26 | [6 empty] | 650 | 656 | 0 | 0 | B_ABIS_ABK1_2 | ABKIR_1 | ABIS |  |  |  |  | 0.0039 | 0.021488 | 0.034228 | 0.016116 | 0.051033 | 0.028062 | 0.031694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابيس | سموحة | ABIS | SMOUHA | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 1*380/88 ACSR CABLE 1*800 1*405 AAAC | 10.659 | 800/1 | 800/1 | 600 | 228.624 | 600 | 0.0012244 | 0.0063454 | 0.20656 | 0.0044891 | 0.013028 | 0.14177 | 0.007314 | 0.59261 | 3.0712 | 0.00042677 | 2.1727 | 6.3057 | 0.00029292 | 3.54 | 1*380/88 ACSR | 3.5 | CABLE 1*800 | 4.659 | 1*405 AAAC | 2.5 |  |  | 656 | 658 | 0 | 0 | B_ABIS_SMOH_1 | ABIS | SMOUHA |  |  |  |  | 0.00060382 | 0.0028926 | 0.0048279 | 0.0021694 | 0.0068698 | 0.0037776 | 0.0042665 | 0.00019445 | 0.0012937 | 0.19844 | 0.00077008 | 0.0012514 | 0.1353 | 0 | 0.00042614 | 0.0021591 | 0.0032912 | 0.0015496 | 0.004907 | 0.0026983 | 0.0030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو قير | سموحة | ABO.KIR | SMOUHA | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 1*380/88 ACSR CABLE 1*800 1*405 AAAC | 28.659 | 600/1 | 800/1 | 600 | 228.624 | 600 | 0.0042926 | 0.021891 | 0.23025 | 0.015646 | 0.048359 | 0.1612 | 0.029256 | 2.0776 | 10.5952 | 0.00047573 | 7.5727 | 23.4057 | 0.00033306 | 14.16 | 1*380/88 ACSR | 3.5 | CABLE 1*800 | 4.659 | 1*405 AAAC | 20.5 |  |  | 650 | 658 | 0 | 0 | B_ABK1_SMOH_1 | ABKIR_1 | SMOUHA |  |  |  |  | 0.00060382 | 0.0028926 | 0.0048279 | 0.0021694 | 0.0068698 | 0.0037776 | 0.0042665 | 0.00019445 | 0.0012937 | 0.19844 | 0.00077008 | 0.0012514 | 0.1353 | 0 | 0.0034943 | 0.017705 | 0.026988 | 0.012707 | 0.040238 | 0.022126 | 0.02499 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سموحة | كرموز | SMOUHA | KARMOS | الاسكندرية وغرب الدلتا | Cable | 1 | 220 | Cable cu oil f 1*800 | 6.9 | 800/1 | 800/1 | 600 | 228.624 | 600 | 0.00031506 | 0.0027087 | 0.25705 | 0.0047188 | 0.0039917 | 0.23377 | 0 | 0.15249 | 1.311 | 0.00053109 | 2.2839 | 1.932 | 0.000483 | 0 | Cable cu oil f 1*800 | 6.9 | [6 empty] | 660 | 670 | 0 | 0 | B_KRMZ_SMOH_1 | SMOUHA | KARMOUZ |  |  |  |  | 0.00031506 | 0.0027087 | 0.25705 | 0.0047188 | 0.0039917 | 0.23377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سموحة | كرموز | SMOUHA | KARMOS | الاسكندرية وغرب الدلتا | Cable | 2 | 220 | Cable cu oil f 1*800 | 6.9 | 800/1 | 800/1 | 600 | 228.624 | 600 | 0.00031506 | 0.0027087 | 0.25705 | 0.0047188 | 0.0039917 | 0.23377 | 0 | 0.15249 | 1.311 | 0.00053109 | 2.2839 | 1.932 | 0.000483 | 0 | Cable cu oil f 1*800 | 6.9 | [6 empty] | 660 | 670 | 0 | 0 | B_KRMZ_SMOH_2 | SMOUHA | KARMOUZ |  |  |  |  | 0.00031506 | 0.0027087 | 0.25705 | 0.0047188 | 0.0039917 | 0.23377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو قير | الدخيلة | ABO.KIR | DEKHELA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 46 | 800/1 | 800/1 | 1000 | 381.04 | 1150 | 0.0047426 | 0.029083 | 0.072358 | 0.012355 | 0.078884 | 0.049649 | 0.056074 | 2.2954 | 14.076 | 0.0001495 | 5.98 | 38.18 | 0.00010258 | 27.14 | 2*405 AAAC | 46 | [6 empty] | 650 | 662 | 0 | 0 | B_ABK1_DEKH_1 | ABKIR_1 | DEKHELA |  |  |  |  | 0.0047426 | 0.029083 | 0.072358 | 0.012355 | 0.078884 | 0.049649 | 0.056074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو قير | الدخيلة | ABO.KIR | DEKHELA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 46 | 800/1 | 800/1 | 1000 | 381.04 | 1150 | 0.0047426 | 0.029083 | 0.072358 | 0.012355 | 0.078884 | 0.049649 | 0.056074 | 2.2954 | 14.076 | 0.0001495 | 5.98 | 38.18 | 0.00010258 | 27.14 | 2*405 AAAC | 46 | [6 empty] | 650 | 662 | 0 | 0 | B_ABK1_DEKH_2 | ABKIR_1 | DEKHELA |  |  |  |  | 0.0047426 | 0.029083 | 0.072358 | 0.012355 | 0.078884 | 0.049649 | 0.056074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | حديد الدخيلة | DEKHELA | HADED-DKHLA | الاسكندرية وغرب الدلتا | Cable | 1 | 220 | CABLE 1*1200 | 0.7 | 1200/1 | 1200/1 | 975 | 371.514 | 1000 | 2.1839e-05 | 0.0002531 | 0.03388 | 0.00010124 | 0.00028926 | 0.017956 | 0 | 0.01057 | 0.1225 | 7e-05 | 0.049 | 0.14 | 3.71e-05 | 0 | CABLE 1*1200 | 0.7 | [6 empty] | 664 | 666 | 0 | 0 | B_ALIR_DEKH_1 | ALXIRON | DEKHELA |  | تابع لمصنع |  |  | 2.1839e-05 | 0.0002531 | 0.03388 | 0.00010124 | 0.00028926 | 0.017956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | حديد الدخيلة | DEKHELA | HADED-DKHLA | الاسكندرية وغرب الدلتا | Cable | 2 | 220 | CABLE 1*1200 | 0.7 | 1200/1 | 1200/1 | 975 | 371.514 | 1000 | 2.1839e-05 | 0.0002531 | 0.03388 | 0.00010124 | 0.00028926 | 0.017956 | 0 | 0.01057 | 0.1225 | 7e-05 | 0.049 | 0.14 | 3.71e-05 | 0 | CABLE 1*1200 | 0.7 | [6 empty] | 664 | 666 | 0 | 0 | B_ALIR_DEKH_2 | ALXIRON | DEKHELA |  | تابع لمصنع |  |  | 2.1839e-05 | 0.0002531 | 0.03388 | 0.00010124 | 0.00028926 | 0.017956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | حديد الدخيلة | DEKHELA | HADED-DKHLA | الاسكندرية وغرب الدلتا | Cable | 3 | 220 | CABLE 1*1200 | 0.67 | 1200/1 | 1200/1 | 975 | 371.514 | 1000 | 2.0903e-05 | 0.00024225 | 0.032428 | 9.6901e-05 | 0.00027686 | 0.017187 | 0 | 0.010117 | 0.11725 | 6.7e-05 | 0.0469 | 0.134 | 3.551e-05 | 0 | CABLE 1*1200 | 0.67 | [6 empty] | 664 | 666 | 0 | 0 | B_ALIR_DEKH_3 | ALXIRON | DEKHELA |  | تابع لمصنع |  |  | 2.0903e-05 | 0.00024225 | 0.032428 | 9.6901e-05 | 0.00027686 | 0.017187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | سيدي كرير | DEKHELA | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 28 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 1.3972 | 8.568 | 9.1e-05 | 3.64 | 23.24 | 6.244e-05 | 16.52 | 2*405 AAAC | 28 | [6 empty] | 664 | 672 | 0 | 0 | B_DEKH_SDKR_1 | SIDIKRER | DEKHELA |  |  |  |  | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الدخيلة | سيدي كرير | DEKHELA | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 28 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 1.3972 | 8.568 | 9.1e-05 | 3.64 | 23.24 | 6.244e-05 | 16.52 | 2*405 AAAC | 28 | [6 empty] | 664 | 672 | 0 | 0 | B_DEKH_SDKR_2 | SIDIKRER | DEKHELA |  |  |  |  | 0.0028868 | 0.017702 | 0.044044 | 0.0075207 | 0.048017 | 0.030221 | 0.034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مطروح | السلوم | MATROUH | SALOUM | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 198 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.020414 | 0.12518 | 0.31145 | 0.053182 | 0.33955 | 0.21371 | 0.24136 | 9.8802 | 60.588 | 0.0006435 | 25.74 | 164.34 | 0.00044154 | 116.82 | 2*405 AAAC | 198 | [6 empty] | 682 | 684 | 0 | -0.25 | B_MMSS_SLUM_1 | MATROHSS | SALLUM |  |  |  |  | 0.020414 | 0.12518 | 0.31145 | 0.053182 | 0.33955 | 0.21371 | 0.24136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مطروح | السلوم | MATROUH | SALOUM | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 198 | 1600/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.020414 | 0.12518 | 0.31145 | 0.053182 | 0.33955 | 0.21371 | 0.24136 | 9.8802 | 60.588 | 0.0006435 | 25.74 | 164.34 | 0.00044154 | 116.82 | 2*405 AAAC | 198 | [6 empty] | 682 | 684 | 0 | -0.25 | B_MMSS_SLUM_2 | MATROHSS | SALLUM |  |  |  |  | 0.020414 | 0.12518 | 0.31145 | 0.053182 | 0.33955 | 0.21371 | 0.24136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع ابو المطامير | الترفيهية | EXT.A.MTMR | BRGARBTRFHA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 48.875 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.005039 | 0.0309 | 0.07688 | 0.013128 | 0.083815 | 0.052752 | 0.059579 | 2.4389 | 14.9558 | 0.00015884 | 6.3537 | 40.5662 | 0.00010899 | 28.8362 | 2*405 AAAC | 48.875 | [6 empty] | 629 | 675 | 0 | 0 | B_MTMR5_TRFIH1 | TARFIHIA | MATMR500 |  |  |  |  | 0.005039 | 0.0309 | 0.07688 | 0.013128 | 0.083815 | 0.052752 | 0.059579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع ابو المطامير | الترفيهية | EXT.A.MTMR | BRGARBTRFHA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 48.875 | 2500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.005039 | 0.0309 | 0.07688 | 0.013128 | 0.083815 | 0.052752 | 0.059579 | 2.4389 | 14.9558 | 0.00015884 | 6.3537 | 40.5662 | 0.00010899 | 28.8362 | 2*405 AAAC | 48.875 | [6 empty] | 629 | 675 | 0 | 0 | B_MTMR5_TRFIH2 | TARFIHIA | MATMR500 |  |  |  |  | 0.005039 | 0.0309 | 0.07688 | 0.013128 | 0.083815 | 0.052752 | 0.059579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الترفيهية | العميد | BRGARBTRFHA | OMAID | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 37.5 | 1600/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0038662 | 0.023709 | 0.058987 | 0.010072 | 0.064308 | 0.040474 | 0.045713 | 1.8713 | 11.475 | 0.00012187 | 4.875 | 31.125 | 8.3625e-05 | 22.125 | 2*405 AAAC | 37.5 | [6 empty] | 675 | 680 | 0 | 0 | B_OMID_TRFH_1 | TARFIHIA | OMAID |  | تم الاتصال بمحطة العميد والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0038662 | 0.023709 | 0.058987 | 0.010072 | 0.064308 | 0.040474 | 0.045713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الترفيهية | العميد | BRGARBTRFHA | OMAID | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 37.5 | 1600/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0038662 | 0.023709 | 0.058987 | 0.010072 | 0.064308 | 0.040474 | 0.045713 | 1.8713 | 11.475 | 0.00012187 | 4.875 | 31.125 | 8.3625e-05 | 22.125 | 2*405 AAAC | 37.5 | [6 empty] | 675 | 680 | 0 | 0 | B_OMID_TRFH_2 | TARFIHIA | OMAID |  | تم الاتصال بمحطة العميد والتاكد من تغيير كل محولات التيار للدوائر الى 1600 امبير |  |  | 0.0038662 | 0.023709 | 0.058987 | 0.010072 | 0.064308 | 0.040474 | 0.045713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طبرق | السلوم | TOBROUK | SALOUM | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 170 | 1600/1 | 1600/1 | 900 | 342.936 | 1200 | 0.017527 | 0.10748 | 0.26741 | 0.045661 | 0.29153 | 0.18348 | 0.20723 | 8.483 | 52.02 | 0.0005525 | 22.1 | 141.1 | 0.0003791 | 100.3 | 2*405 AAAC | 170 | [6 empty] | 98 | 684 | 0 | 0 | B_SLUM_TOBK_1 | TOBROK | SALLUM |  | محول تيار, طول الجزء الخاص بمصر 29.1 كم وعدد ابراجه 90 برج اما العدد الكلي للابراج بما فيها الجانب الليبي 514 برج |  |  | 0.017527 | 0.10748 | 0.26741 | 0.045661 | 0.29153 | 0.18348 | 0.20723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طبرق | السلوم | TOBROUK | SALOUM | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 170 | 1600/1 | 1600/1 | 900 | 342.936 | 1200 | 0.017527 | 0.10748 | 0.26741 | 0.045661 | 0.29153 | 0.18348 | 0.20723 | 8.483 | 52.02 | 0.0005525 | 22.1 | 141.1 | 0.0003791 | 100.3 | 2*405 AAAC | 170 | [6 empty] | 98 | 684 | 0 | 0 | B_SLUM_TOBK_2 | TOBROK | SALLUM |  | محول تيار, طول الجزء الخاص بمصر 29.1 كم وعدد ابراجه 90 برج اما العدد الكلي للابراج بما فيها الجانب الليبي 514 برج |  |  | 0.017527 | 0.10748 | 0.26741 | 0.045661 | 0.29153 | 0.18348 | 0.20723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السيوف | ابيس | SUIF | ABIS | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 6.7 | 1600/1 | 800/1 | 800 | 304.832 | 1150 | 0.00069076 | 0.004236 | 0.010539 | 0.0017996 | 0.01149 | 0.0072314 | 0.0081674 | 0.33433 | 2.0502 | 2.1775e-05 | 0.871 | 5.561 | 1.4941e-05 | 3.953 | 2*405 AAAC | 6.7 | [6 empty] | 654 | 656 | 0 | 0 | B_ABIS_SIUF_1 | SIUF_PS | ABIS |  | محول تيار |  |  | 0.00069076 | 0.004236 | 0.010539 | 0.0017996 | 0.01149 | 0.0072314 | 0.0081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السيوف | ابيس | SUIF | ABIS | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 6.7 | 1600/1 | 800/1 | 800 | 304.832 | 1150 | 0.00069076 | 0.004236 | 0.010539 | 0.0017996 | 0.01149 | 0.0072314 | 0.0081674 | 0.33433 | 2.0502 | 2.1775e-05 | 0.871 | 5.561 | 1.4941e-05 | 3.953 | 2*405 AAAC | 6.7 | [6 empty] | 654 | 656 | 0 | 0 | B_ABIS_SIUF_2 | SIUF_PS | ABIS |  | محول تيار |  |  | 0.00069076 | 0.004236 | 0.010539 | 0.0017996 | 0.01149 | 0.0072314 | 0.0081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الدوار | ابيس | KAFR-DAWAR | ABIS | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*375.2/87 MCM 461 | 23 | 1200/1 | 1600/1 | 1200 | 457.248 | 1300 | 0.0035094 | 0.028261 | 0.082822 | 0.035736 | 0.089339 | 0.049148 | 0.055504 | 1.6986 | 13.6781 | 0.00017112 | 17.296 | 43.24 | 0.00010155 | 26.864 | 1*375.2/87 MCM 461 | 23 | [6 empty] | 608 | 656 | 0 | 0 | B_ABIS_KDWR_1 | KDAWAR | ABIS |  |  |  |  | 0.0035094 | 0.028261 | 0.082822 | 0.035736 | 0.089339 | 0.049148 | 0.055504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الدوار | ابيس | KAFR-DAWAR | ABIS | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*375.2/87 MCM 461 | 23 | 1200/1 | 1600/1 | 1200 | 457.248 | 1300 | 0.0035094 | 0.028261 | 0.082822 | 0.035736 | 0.089339 | 0.049148 | 0.055504 | 1.6986 | 13.6781 | 0.00017112 | 17.296 | 43.24 | 0.00010155 | 26.864 | 1*375.2/87 MCM 461 | 23 | [6 empty] | 608 | 656 | 0 | 0 | B_ABIS_KDWR_2 | KDAWAR | ABIS |  |  |  |  | 0.0035094 | 0.028261 | 0.082822 | 0.035736 | 0.089339 | 0.049148 | 0.055504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
أبو قير | السيوف | ABO.KIR | SUIF | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 23.3 | 1200/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0024022 | 0.014731 | 0.036651 | 0.0062583 | 0.039957 | 0.025148 | 0.028403 | 1.1627 | 7.1298 | 7.5725e-05 | 3.029 | 19.339 | 5.1959e-05 | 13.747 | 2*405 AAAC | 23.3 | [6 empty] | 650 | 654 | 0 | 0 | B_ABK2_SIUF_1 | ABKIR_2 | SIUF_PS |  |  |  |  | 0.0024022 | 0.014731 | 0.036651 | 0.0062583 | 0.039957 | 0.025148 | 0.028403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
أبو قير | السيوف | ABO.KIR | SUIF | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 23.3 | 1200/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0024022 | 0.014731 | 0.036651 | 0.0062583 | 0.039957 | 0.025148 | 0.028403 | 1.1627 | 7.1298 | 7.5725e-05 | 3.029 | 19.339 | 5.1959e-05 | 13.747 | 2*405 AAAC | 23.3 | [6 empty] | 650 | 654 | 0 | 0 | B_ABK2_SIUF_2 | ABKIR_2 | SIUF_PS |  |  |  |  | 0.0024022 | 0.014731 | 0.036651 | 0.0062583 | 0.039957 | 0.025148 | 0.028403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كرموز | سيدي كرير | KARMOS | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 37 | 1600/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 1.8463 | 11.322 | 0.00012025 | 4.81 | 30.71 | 8.251e-05 | 21.83 | 2*405 AAAC | 37 | [6 empty] | 670 | 672 | 0 | 0 | B_KRMZ_SDKR_1 | KARMOUZ | SIDIKRER |  |  |  |  | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كرموز | سيدي كرير | KARMOS | SIDI-KRIR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 37 | 1600/1 | 2500/1 | 1150 | 438.196 | 1150 | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 1.8463 | 11.322 | 0.00012025 | 4.81 | 30.71 | 8.251e-05 | 21.83 | 2*405 AAAC | 37 | [6 empty] | 670 | 672 | 0 | 0 | B_KRMZ_SDKR_2 | KARMOUZ | SIDIKRER |  |  |  |  | 0.0038147 | 0.023393 | 0.058201 | 0.009938 | 0.06345 | 0.039935 | 0.045103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سيدي كرير | برج العرب | SIDI-KRIR | BRG-ARB | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC | 25 | 3000/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 1.2475 | 7.65 | 8.125e-05 | 3.25 | 20.75 | 5.575e-05 | 14.75 | 2*405 AAAC | 25 | [6 empty] | 672 | 674 | 0 | 0 | B_BARB_SDKR_1 | SIDIKRER | BORGARB |  |  |  |  | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سيدي كرير | برج العرب | SIDI-KRIR | BRG-ARB | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC | 25 | 3000/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 1.2475 | 7.65 | 8.125e-05 | 3.25 | 20.75 | 5.575e-05 | 14.75 | 2*405 AAAC | 25 | [6 empty] | 672 | 674 | 0 | 0 | B_BARB_SDKR_2 | SIDIKRER | BORGARB |  |  |  |  | 0.0025775 | 0.015806 | 0.039325 | 0.0067149 | 0.042872 | 0.026983 | 0.030475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور GIS | كفر الدوار | DMNHOR-GIS | KAFR-DAWAR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR 2*405 AAAC | 23.5 | 1200/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0020717 | 0.014696 | 0.04141 | 0.0055047 | 0.045143 | 0.025364 | 0.028647 | 1.0027 | 7.1129 | 8.5557e-05 | 2.6643 | 21.8493 | 5.2405e-05 | 13.865 | 2*380/50 ACSR | 19.536 | 2*405 AAAC | 3.964 |  |  |  |  | 606 | 608 | 0 | 0 | B_DMN2_KDWR_1 | DAMNHOR2 | KDAWAR |  |  |  |  | 0.001663 | 0.01219 | 0.035174 | 0.00444 | 0.038345 | 0.021086 | 0.023815 | 0.00040869 | 0.0025062 | 0.0062354 | 0.0010647 | 0.0067978 | 0.0042784 | 0.0048321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور GIS | كفر الدوار | DMNHOR-GIS | KAFR-DAWAR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR 2*405 AAAC | 23.5 | 1200/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0020717 | 0.014696 | 0.04141 | 0.0055047 | 0.045143 | 0.025364 | 0.028647 | 1.0027 | 7.1129 | 8.5557e-05 | 2.6643 | 21.8493 | 5.2405e-05 | 13.865 | 2*380/50 ACSR | 19.536 | 2*405 AAAC | 3.964 |  |  |  |  | 606 | 608 | 0 | 0 | B_DMN2_KDWR_2 | DAMNHOR2 | KDAWAR |  |  |  |  | 0.001663 | 0.01219 | 0.035174 | 0.00444 | 0.038345 | 0.021086 | 0.023815 | 0.00040869 | 0.0025062 | 0.0062354 | 0.0010647 | 0.0067978 | 0.0042784 | 0.0048321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور الغازية | توسيع ايتاي | DMNHR-G | ETY-BARD | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 44 | 1500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0088178 | 0.036881 | 0.058995 | 0.02574 | 0.10561 | 0.039863 | 0.066013 | 4.2678 | 17.8504 | 0.00012189 | 12.4581 | 51.1136 | 8.2362e-05 | 31.9501 | Thermal Stacir 1*238/97 | 32.244 | 2*405 AAAC | 11.756 |  |  |  |  | 604 | 612 | 0 | 0 | B_DMN1_EBRD_1 | DAMNHOR1 | ETAY500 |  |  |  |  | 0.0076058 | 0.029448 | 0.040503 | 0.022582 | 0.085447 | 0.027175 | 0.051682 | 0.001212 | 0.0074325 | 0.018492 | 0.0031576 | 0.02016 | 0.012688 | 0.014331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور الغازية | توسيع ايتاي | DMNHR-G | ETY-BARD | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | Thermal Stacir 1*238/97 2*405 AAAC | 44 | 1500/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0088178 | 0.036881 | 0.058995 | 0.02574 | 0.10561 | 0.039863 | 0.066013 | 4.2678 | 17.8504 | 0.00012189 | 12.4581 | 51.1136 | 8.2362e-05 | 31.9501 | Thermal Stacir 1*238/97 | 32.244 | 2*405 AAAC | 11.756 |  |  |  |  | 604 | 612 | 0 | 0 | B_DMN1_EBRD_2 | DAMNHOR1 | ETAY500 |  |  |  |  | 0.0076058 | 0.029448 | 0.040503 | 0.022582 | 0.085447 | 0.027175 | 0.051682 | 0.001212 | 0.0074325 | 0.018492 | 0.0031576 | 0.02016 | 0.012688 | 0.014331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور الغازية | دمنهور GIS | DMNHR-G | DMNHOR-GIS | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*507 AAAC | 2 | 1200/1 | 1200/1 | 1200 | 457.248 | 1500 | 0.00015289 | 0.0012314 | 0.0036397 | 0.0015702 | 0.0039256 | 0.0021586 | 0.002438 | 0.074 | 0.596 | 7.52e-06 | 0.76 | 1.9 | 4.46e-06 | 1.18 | 2*507 AAAC | 2 | [6 empty] | 604 | 606 | 0 | 0 | B_DMN1_DMN2_1 | DAMNHOR1 | DAMNHOR2 |  | محول تيار |  |  | 0.00015289 | 0.0012314 | 0.0036397 | 0.0015702 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمنهور الغازية | دمنهور GIS | DMNHR-G | DMNHOR-GIS | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*507 AAAC | 2 | 1500/1 | 1200/1 | 1200 | 457.248 | 1500 | 0.00015289 | 0.0012314 | 0.0036397 | 0.0015702 | 0.0039256 | 0.0021586 | 0.002438 | 0.074 | 0.596 | 7.52e-06 | 0.76 | 1.9 | 4.46e-06 | 1.18 | 2*507 AAAC | 2 | [6 empty] | 604 | 606 | 0 | 0 | B_DMN1_DMN2_2 | DAMNHOR1 | DAMNHOR2 |  | محول تيار |  |  | 0.00015289 | 0.0012314 | 0.0036397 | 0.0015702 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحمودية الجديدة | دمنهور الغازية | N.MHMODIA | DMNHR-G | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*380/88 ACSR | 15 | 2000/1 | 600/1 | 500 | 190.52 | 670 | 0.0025878 | 0.012397 | 0.020691 | 0.0092975 | 0.029442 | 0.01619 | 0.018285 | 1.2525 | 6 | 4.275e-05 | 4.5 | 14.25 | 3.345e-05 | 8.85 | 1*380/88 ACSR | 15 | [6 empty] | 602 | 604 | 0 | 0 | B_DMN1_NMHM_1 | NMHMODIA | DAMNHOR1 |  |  |  |  | 0.0025878 | 0.012397 | 0.020691 | 0.0092975 | 0.029442 | 0.01619 | 0.018285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المحمودية الجديدة | دمنهور الغازية | N.MHMODIA | DMNHR-G | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*380/88 ACSR | 15 | 2000/1 | 600/1 | 500 | 190.52 | 670 | 0.0025878 | 0.012397 | 0.020691 | 0.0092975 | 0.029442 | 0.01619 | 0.018285 | 1.2525 | 6 | 4.275e-05 | 4.5 | 14.25 | 3.345e-05 | 8.85 | 1*380/88 ACSR | 15 | [6 empty] | 602 | 604 | 0 | 0 | B_DMN1_NMHMD_2 | NMHMODIA | DAMNHOR1 |  |  |  |  | 0.0025878 | 0.012397 | 0.020691 | 0.0092975 | 0.029442 | 0.01619 | 0.018285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | التحرير بدر | MENOUF | TAHRIR-BADR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 47 | 800/1 | 1600/1 | 250 | 95.26 | 670 | 0.0066227 | 0.035401 | 0.07199 | 0.022459 | 0.092252 | 0.050728 | 0.057293 | 3.2054 | 17.134 | 0.00014874 | 10.87 | 44.65 | 0.00010481 | 27.73 | 1*380/88 ACSR | 30 | 2*380/50 ACSR | 17 |  |  |  |  | 526 | 614 | 0 | 0 | B_MNOF_TBDR_1 | MENOUF | THRIRBDR |  | تهالك بعد مخاطبة م حمدي خليفة تم الاتصال ب م حمادة في نوفمبر 2020 بمحطة التحرير بدر وافاد ان محولات التيار لدوائر منوف وايتاي 1600 امبير وللرابط 2000 امبير |  |  | 0.0051756 | 0.024793 | 0.041382 | 0.018595 | 0.058884 | 0.03238 | 0.03657 | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | التحرير بدر | MENOUF | TAHRIR-BADR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 47 | 800/1 | 1600/1 | 250 | 95.26 | 670 | 0.0066227 | 0.035401 | 0.07199 | 0.022459 | 0.092252 | 0.050728 | 0.057293 | 3.2054 | 17.134 | 0.00014874 | 10.87 | 44.65 | 0.00010481 | 27.73 | 1*380/88 ACSR | 30 | 2*380/50 ACSR | 17 |  |  |  |  | 526 | 614 | 0 | 0 | B_MNOF_TBDR_2 | MENOUF | THRIRBDR |  |  |  |  | 0.0051756 | 0.024793 | 0.041382 | 0.018595 | 0.058884 | 0.03238 | 0.03657 | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | التحرير بدر | ETY-BARD | TAHRIR-BADR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC Thermal Invar 1*255/88 | 46.5 | 1600/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0092806 | 0.038896 | 0.062439 | 0.027078 | 0.11134 | 0.042196 | 0.069653 | 4.4918 | 18.8255 | 0.00012901 | 13.1057 | 53.8874 | 8.7182e-05 | 33.712 | 2*405 AAAC | 12.712 | Thermal Invar 1*255/88 | 33.788 |  |  |  |  | 611 | 613 | 0 | 0 | B_EBRD_TBDR_1 | ETAYBARD | THRIRBDR |  | تم الاتصال ب م حمادة في نوفمبر 2020 بمحطة التحرير بدر وافاد ان محولات التيار لدوائر منوف وايتاي 1600 امبير وللرابط 2000 امبير |  |  | 0.0013106 | 0.0080369 | 0.019996 | 0.0034144 | 0.0218 | 0.01372 | 0.015496 | 0.00797 | 0.030859 | 0.042443 | 0.023664 | 0.089538 | 0.028476 | 0.054157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | التحرير بدر | ETY-BARD | TAHRIR-BADR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC Thermal Invar 1*255/88 | 46.5 | 1600/1 | 1600/1 | 1150 | 438.196 | 1150 | 0.0092806 | 0.038896 | 0.062439 | 0.027078 | 0.11134 | 0.042196 | 0.069653 | 4.4918 | 18.8255 | 0.00012901 | 13.1057 | 53.8874 | 8.7182e-05 | 33.712 | 2*405 AAAC | 12.712 | Thermal Invar 1*255/88 | 33.788 |  |  |  |  | 611 | 613 | 0 | 0 | B_EBRD_TBDR_2 | ETAYBARD | THRIRBDR |  |  |  |  | 0.0013106 | 0.0080369 | 0.019996 | 0.0034144 | 0.0218 | 0.01372 | 0.015496 | 0.00797 | 0.030859 | 0.042443 | 0.023664 | 0.089538 | 0.028476 | 0.054157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | السادات | BOSTAN | SADAT | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR | 35 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0076227 | 0.03075 | 0.046251 | 0.022525 | 0.089864 | 0.030491 | 0.054487 | 3.6894 | 14.8832 | 9.556e-05 | 10.9023 | 43.4941 | 6.2998e-05 | 26.3719 | Thermal Invar 1*255/88 | 30.8 | 2*380/50 ACSR | 4.2 |  |  |  |  | 616 | 626 | 0 | 0 | B_BOST_SDAT_1 | BOSTAN | SADAT |  |  |  |  | 0.0072652 | 0.02813 | 0.038689 | 0.021571 | 0.08162 | 0.025958 | 0.049367 | 0.00035752 | 0.0026207 | 0.007562 | 0.00095455 | 0.0082438 | 0.0045331 | 0.0051198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | السادات | BOSTAN | SADAT | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR | 35 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0076227 | 0.03075 | 0.046251 | 0.022525 | 0.089864 | 0.030491 | 0.054487 | 3.6894 | 14.8832 | 9.556e-05 | 10.9023 | 43.4941 | 6.2998e-05 | 26.3719 | Thermal Invar 1*255/88 | 30.8 | 2*380/50 ACSR | 4.2 |  |  |  |  | 616 | 626 | 0 | 0 | B_BOST_SDAT_1 | BOSTAN | SADAT |  |  |  |  | 0.0072652 | 0.02813 | 0.038689 | 0.021571 | 0.08162 | 0.025958 | 0.049367 | 0.00035752 | 0.0026207 | 0.007562 | 0.00095455 | 0.0082438 | 0.0045331 | 0.0051198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | المتميز | BOSTAN | MOTAMAYEZ | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | Thermal Invar 1*255/88 3*380/50 ACSR | 27.3 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0058664 | 0.024022 | 0.036274 | 0.01855 | 0.06923 | 0.024719 | 0.040375 | 2.8394 | 11.6265 | 7.4947e-05 | 8.978 | 33.5072 | 5.1073e-05 | 19.5413 | Thermal Invar 1*255/88 | 24.3 | 3*380/50 ACSR | 3 |  |  |  |  | 616 | 625 | 0 | 0 | B_BOST_MTMZ_2 | BOSTAN | H_MOTMIZ |  |  |  |  | 0.0057319 | 0.022193 | 0.030524 | 0.017019 | 0.064395 | 0.02048 | 0.038949 | 0.0001345 | 0.0018285 | 0.0057499 | 0.001531 | 0.0048347 | 0.0042398 | 0.0014256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | المتميز | BOSTAN | MOTAMAYEZ | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | Thermal Invar 1*255/88 3*380/50 ACSR | 27.3 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0058664 | 0.024022 | 0.036274 | 0.01855 | 0.06923 | 0.024719 | 0.040375 | 2.8394 | 11.6265 | 7.4947e-05 | 8.978 | 33.5072 | 5.1073e-05 | 19.5413 | Thermal Invar 1*255/88 | 24.3 | 3*380/50 ACSR | 3 |  |  |  |  | 616 | 625 | 0 | 0 | B_BOST_MTMZ_2 | BOSTAN | H_MOTMIZ |  |  |  |  | 0.0057319 | 0.022193 | 0.030524 | 0.017019 | 0.064395 | 0.02048 | 0.038949 | 0.0001345 | 0.0018285 | 0.0057499 | 0.001531 | 0.0048347 | 0.0042398 | 0.0014256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المتميز | وادي النطرون | MOTAMAYEZ | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 3*380/50 ACSR | 31 | 1600/1 | 2500/1 | 1600 | 609.664 | 1800 | 0.0013899 | 0.018895 | 0.059416 | 0.01582 | 0.049959 | 0.043812 | 0.014731 | 0.6727 | 9.145 | 0.00012276 | 7.657 | 24.18 | 9.052e-05 | 7.13 | 3*380/50 ACSR | 31 | [6 empty] | 625 | 630 | 0 | 0 | B_NTRON_MTMZ_1 | H_MOTMIZ | W_NATRON |  |  |  |  | 0.0013899 | 0.018895 | 0.059416 | 0.01582 | 0.049959 | 0.043812 | 0.014731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المتميز | وادي النطرون | MOTAMAYEZ | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 31 | 1600/1 | 2500/1 | 1600 | 609.664 | 1800 | 0.0013899 | 0.018895 | 0.059416 | 0.01582 | 0.049959 | 0.043812 | 0.014731 | 0.6727 | 9.145 | 0.00012276 | 7.657 | 24.18 | 9.052e-05 | 7.13 | 3*380/50 ACSR | 31 | [6 empty] | 625 | 630 | 0 | 0 | B_NTRON_MTMZ_2 | H_MOTMIZ | W_NATRON |  |  |  |  | 0.0013899 | 0.018895 | 0.059416 | 0.01582 | 0.049959 | 0.043812 | 0.014731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | ابو المطامير | BOSTAN | A.MATAMR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR Thermal Invar 431 mm | 37 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0082151 | 0.032808 | 0.048328 | 0.024305 | 0.095714 | 0.031987 | 0.058 | 3.9761 | 15.8793 | 9.9851e-05 | 11.7634 | 46.3254 | 6.6089e-05 | 28.072 | 2*380/50 ACSR | 3.4 | Thermal Invar 431 mm | 33.6 |  |  |  |  | 616 | 628 | 0 | 0 | B_BOST_TMAT_1 | BOSTAN | TMTAMIR |  |  |  |  | 0.00028942 | 0.0021215 | 0.0061216 | 0.00077273 | 0.0066736 | 0.0036697 | 0.0041446 | 0.0079256 | 0.030687 | 0.042206 | 0.023532 | 0.08904 | 0.028318 | 0.053855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | ابو المطامير | BOSTAN | A.MATAMR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR Thermal Invar 431 mm | 37 | 1200/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0082151 | 0.032808 | 0.048328 | 0.024305 | 0.095714 | 0.031987 | 0.058 | 3.9761 | 15.8793 | 9.9851e-05 | 11.7634 | 46.3254 | 6.6089e-05 | 28.072 | 2*380/50 ACSR | 3.4 | Thermal Invar 431 mm | 33.6 |  |  |  |  | 616 | 628 | 0 | 0 | B_BOST_TMAT_2 | BOSTAN | TMTAMIR |  |  |  |  | 0.00028942 | 0.0021215 | 0.0061216 | 0.00077273 | 0.0066736 | 0.0036697 | 0.0041446 | 0.0079256 | 0.030687 | 0.042206 | 0.023532 | 0.08904 | 0.028318 | 0.053855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | البستان | ETY-BARD | BOSTAN | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 60 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 2.472 | 18.12 | 0.0002232 | 6.6 | 57 | 0.0001338 | 35.4 | 2*380/50 ACSR | 60 | [6 empty] | 611 | 616 | 0 | 0 | B_BOST_EBRD_1 | ETAYBARD | BOSTAN |  |  |  |  | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | البستان | ETY-BARD | BOSTAN | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 60 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 2.472 | 18.12 | 0.0002232 | 6.6 | 57 | 0.0001338 | 35.4 | 2*380/50 ACSR | 60 | [6 empty] | 611 | 616 | 0 | 0 | B_BOST_EBRD_2 | ETAYBARD | BOSTAN |  |  |  |  | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | النوبارية | BOSTAN | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 56 | 1200/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0047669 | 0.034942 | 0.10083 | 0.012727 | 0.10992 | 0.060442 | 0.068264 | 2.3072 | 16.912 | 0.00020832 | 6.16 | 53.2 | 0.00012488 | 33.04 | 2*380/50 ACSR | 56 | [6 empty] | 616 | 618 | 0 | 0 | B_BOST_NBRI_1 | BOSTAN | NOBARIA |  |  |  |  | 0.0047669 | 0.034942 | 0.10083 | 0.012727 | 0.10992 | 0.060442 | 0.068264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
البستان | النوبارية | BOSTAN | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 56 | 1200/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0047669 | 0.034942 | 0.10083 | 0.012727 | 0.10992 | 0.060442 | 0.068264 | 2.3072 | 16.912 | 0.00020832 | 6.16 | 53.2 | 0.00012488 | 33.04 | 2*380/50 ACSR | 56 | [6 empty] | 616 | 618 | 0 | 0 | B_BOST_NBRI_2 | BOSTAN | NOBARIA |  |  |  |  | 0.0047669 | 0.034942 | 0.10083 | 0.012727 | 0.10992 | 0.060442 | 0.068264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العز | السادات | AL-EZZ | SADAT | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 6 | 1000/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0.2472 | 1.812 | 2.232e-05 | 0.66 | 5.7 | 1.338e-05 | 3.54 | 2*380/50 ACSR | 6 | [6 empty] | 624 | 626 | 0 | 0 | B_EZZ_SDAT_1 | EL_EZZ | SADAT |  | محول تيار من جهة العز وتم التاكد من م علاء بمحطة العز في نوفمبر 2020 |  |  | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العز | السادات | AL-EZZ | SADAT | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 6 | 1000/1 | 1600/1 | 1000 | 381.04 | 1200 | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0.2472 | 1.812 | 2.232e-05 | 0.66 | 5.7 | 1.338e-05 | 3.54 | 2*380/50 ACSR | 6 | [6 empty] | 624 | 626 | 0 | 0 | B_EZZ_SDAT_2 | EL_EZZ | SADAT |  | محول تيار من جهة العز وتم التاكد من م علاء بمحطة العز في نوفمبر 2020 |  |  | 0.00051074 | 0.0037438 | 0.010803 | 0.0013636 | 0.011777 | 0.0064759 | 0.007314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اركوستيل | العز | ARCOSTEL | AL-EZZ | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 0.4 | 1000/1 | 1000/1 | 1000 | 381.04 | 1200 | 3.405e-05 | 0.00024959 | 0.00072019 | 9.0909e-05 | 0.00078512 | 0.00043173 | 0.0004876 | 0.01648 | 0.1208 | 1.488e-06 | 0.044 | 0.38 | 8.92e-07 | 0.236 | 2*380/50 ACSR | 0.4 | [6 empty] | 622 | 624 | 0 | 0 | B_ARCS_EZZ_1 | ARCSTEEL | EL_EZZ |  | محول تيار من جهة العز وتم التاكد من م علاء بمحطة العز في نوفمبر 2020 محول تيارمن جهة اركوستيل هو 1000 امبير تم التاكد من المحطة يوم 2 نوفمبر 2020 |  |  | 3.405e-05 | 0.00024959 | 0.00072019 | 9.0909e-05 | 0.00078512 | 0.00043173 | 0.0004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اركوستيل | العز | ARCOSTEL | AL-EZZ | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 0.4 | 1000/1 | 1000/1 | 1000 | 381.04 | 1200 | 3.405e-05 | 0.00024959 | 0.00072019 | 9.0909e-05 | 0.00078512 | 0.00043173 | 0.0004876 | 0.01648 | 0.1208 | 1.488e-06 | 0.044 | 0.38 | 8.92e-07 | 0.236 | 2*380/50 ACSR | 0.4 | [6 empty] | 622 | 624 | 0 | 0 | B_ARCS_EZZ_2 | ARCSTEEL | EL_EZZ |  |  |  |  | 3.405e-05 | 0.00024959 | 0.00072019 | 9.0909e-05 | 0.00078512 | 0.00043173 | 0.0004876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المصرية الامريكية | اركوستيل | MSR-AMR | ARCOSTEL | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 1.4 | 1200/1 | 1000/1 | 1000 | 381.04 | 1200 | 0.00011917 | 0.00087355 | 0.0025207 | 0.00031818 | 0.0027479 | 0.001511 | 0.0017066 | 0.05768 | 0.4228 | 5.208e-06 | 0.154 | 1.33 | 3.122e-06 | 0.826 | 2*380/50 ACSR | 1.4 | [6 empty] | 620 | 622 | 0 | 0 | B_ARCS_EGAM_1 | EGYAMR | ARCSTEEL |  | محول تيارمن جهة اركوستيل هو 1000 امبير تم التاكد من المحطة يوم 2 نوفمبر 2020 |  |  | 0.00011917 | 0.00087355 | 0.0025207 | 0.00031818 | 0.0027479 | 0.001511 | 0.0017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المصرية الامريكية | اركوستيل | MSR-AMR | ARCOSTEL | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 1.4 | 1200/1 | 1000/1 | 1000 | 381.04 | 1200 | 0.00011917 | 0.00087355 | 0.0025207 | 0.00031818 | 0.0027479 | 0.001511 | 0.0017066 | 0.05768 | 0.4228 | 5.208e-06 | 0.154 | 1.33 | 3.122e-06 | 0.826 | 2*380/50 ACSR | 1.4 | [6 empty] | 620 | 622 | 0 | 0 | B_ARCS_EGAM_2 | EGYAMR | ARCSTEEL |  | محول تيارمن جهة اركوستيل هو 1000 امبير تم التاكد من المحطة يوم 2 نوفمبر 2020 |  |  | 0.00011917 | 0.00087355 | 0.0025207 | 0.00031818 | 0.0027479 | 0.001511 | 0.0017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المصرية الامريكية | وادي النطرون | MSR-AMR | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 30 | 1200/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 1.236 | 9.06 | 0.0001116 | 3.3 | 28.5 | 6.69e-05 | 17.7 | 2*380/50 ACSR | 30 | [6 empty] | 620 | 630 | 0 | 0 | B_EGAM_NTRON_1 | EGYAMR | W-NATRON |  |  |  |  | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المصرية الامريكية | وادي النطرون | MSR-AMR | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 30 | 1200/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 1.236 | 9.06 | 0.0001116 | 3.3 | 28.5 | 6.69e-05 | 17.7 | 2*380/50 ACSR | 30 | [6 empty] | 620 | 630 | 0 | 0 | B_EGAM_NTRON_2 | EGYAMR | W-NATRON |  |  |  |  | 0.0025537 | 0.018719 | 0.054014 | 0.0068182 | 0.058884 | 0.03238 | 0.03657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشيخ زايد | وادي النطرون | ZAID | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 36.5 | 1200/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.003107 | 0.022775 | 0.065718 | 0.0082955 | 0.071643 | 0.039395 | 0.044494 | 1.5038 | 11.023 | 0.00013578 | 4.015 | 34.675 | 8.1395e-05 | 21.535 | 2*380/50 ACSR | 36.5 | [6 empty] | 414 | 630 | 0 | 0 | B_NATRON_ZYD_1 | ZAYD | W_NATRON |  |  |  |  | 0.003107 | 0.022775 | 0.065718 | 0.0082955 | 0.071643 | 0.039395 | 0.044494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الشيخ زايد | وادي النطرون | ZAID | WADI-NATRON | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 36.5 | 1200/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.003107 | 0.022775 | 0.065718 | 0.0082955 | 0.071643 | 0.039395 | 0.044494 | 1.5038 | 11.023 | 0.00013578 | 4.015 | 34.675 | 8.1395e-05 | 21.535 | 2*380/50 ACSR | 36.5 | [6 empty] | 414 | 630 | 0 | 0 | B_NATRON_ZYD_2 | ZAYD | W_NATRON |  |  |  |  | 0.003107 | 0.022775 | 0.065718 | 0.0082955 | 0.071643 | 0.039395 | 0.044494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النطرون | الرمي الجوي | WADI-NATRON | RMY.ELGWY | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 40.768 | 2500/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0034703 | 0.025438 | 0.073402 | 0.0092655 | 0.08002 | 0.044002 | 0.049697 | 1.6796 | 12.3119 | 0.00015166 | 4.4845 | 38.7296 | 9.0913e-05 | 24.0531 | 2*380/50 ACSR | 40.768 | [6 empty] | 630 | 632 | 0 | 0 | B_GAWY_NTRON_1 | W_NATRON | RAMY_GWY |  |  |  |  | 0.0034703 | 0.025438 | 0.073402 | 0.0092655 | 0.08002 | 0.044002 | 0.049697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النطرون | الرمي الجوي | WADI-NATRON | RMY.ELGWY | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 40.768 | 2500/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0034703 | 0.025438 | 0.073402 | 0.0092655 | 0.08002 | 0.044002 | 0.049697 | 1.6796 | 12.3119 | 0.00015166 | 4.4845 | 38.7296 | 9.0913e-05 | 24.0531 | 2*380/50 ACSR | 40.768 | [6 empty] | 630 | 632 | 0 | 0 | B_GAWY_NTRON_2 | W_NATRON | RAMY_GWY |  |  |  |  | 0.0034703 | 0.025438 | 0.073402 | 0.0092655 | 0.08002 | 0.044002 | 0.049697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | الرمي الجوي | RABT ( RAMY, ND1, ND2) | RMY.ELGWY | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 60 | NO C.T | 2000/1 | 1800 | 685.872 | 1800 | 0.0026901 | 0.03657 | 0.115 | 0.03062 | 0.096694 | 0.084797 | 0.028512 | 1.302 | 17.7 | 0.0002376 | 14.82 | 46.8 | 0.0001752 | 13.8 | 3*380/50 ACSR | 60 | [7 empty] | 632 | 0 | 0 |  |  | RAMY_GWY |  |  |  |  | 0.0026901 | 0.03657 | 0.115 | 0.03062 | 0.096694 | 0.084797 | 0.028512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | الرمي الجوي | RABT ( RAMY, ND1, ND2) | RMY.ELGWY | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 60 | NO C.T | 2000/1 | 1800 | 685.872 | 1800 | 0.0026901 | 0.03657 | 0.115 | 0.03062 | 0.096694 | 0.084797 | 0.028512 | 1.302 | 17.7 | 0.0002376 | 14.82 | 46.8 | 0.0001752 | 13.8 | 3*380/50 ACSR | 60 | [7 empty] | 632 | 0 | 0 |  |  | RAMY_GWY |  |  |  |  | 0.0026901 | 0.03657 | 0.115 | 0.03062 | 0.096694 | 0.084797 | 0.028512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | ND2 | RABT ( RAMY, ND1, ND2) | ND2 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 5 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.00022417 | 0.0030475 | 0.0095832 | 0.0025517 | 0.0080579 | 0.0070664 | 0.002376 | 0.1085 | 1.475 | 1.98e-05 | 1.235 | 3.9 | 1.46e-05 | 1.15 | 3*380/50 ACSR | 5 | [8 empty] | 0 | 0 | [7 empty] | 0.00022417 | 0.0030475 | 0.0095832 | 0.0025517 | 0.0080579 | 0.0070664 | 0.002376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | ND2 | RABT ( RAMY, ND1, ND2) | ND2 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 5 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.00022417 | 0.0030475 | 0.0095832 | 0.0025517 | 0.0080579 | 0.0070664 | 0.002376 | 0.1085 | 1.475 | 1.98e-05 | 1.235 | 3.9 | 1.46e-05 | 1.15 | 3*380/50 ACSR | 5 | [8 empty] | 0 | 0 | [7 empty] | 0.00022417 | 0.0030475 | 0.0095832 | 0.0025517 | 0.0080579 | 0.0070664 | 0.002376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | ND1 | RABT ( RAMY, ND1, ND2) | ND1 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 34.4 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.0015423 | 0.020967 | 0.065932 | 0.017555 | 0.055438 | 0.048617 | 0.016347 | 0.74648 | 10.148 | 0.00013622 | 8.4968 | 26.832 | 0.00010045 | 7.912 | 3*380/50 ACSR | 34.4 | [8 empty] | 0 | 0 | [7 empty] | 0.0015423 | 0.020967 | 0.065932 | 0.017555 | 0.055438 | 0.048617 | 0.016347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط ( الرمي الجوي , ND1 , ND2 ) | ND1 | RABT ( RAMY, ND1, ND2) | ND1 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 34.4 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.0015423 | 0.020967 | 0.065932 | 0.017555 | 0.055438 | 0.048617 | 0.016347 | 0.74648 | 10.148 | 0.00013622 | 8.4968 | 26.832 | 0.00010045 | 7.912 | 3*380/50 ACSR | 34.4 | [8 empty] | 0 | 0 | [7 empty] | 0.0015423 | 0.020967 | 0.065932 | 0.017555 | 0.055438 | 0.048617 | 0.016347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HPS12 | ND1 | HPS12 | ND1 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 8 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.00035868 | 0.004876 | 0.015333 | 0.0040826 | 0.012893 | 0.011306 | 0.0038017 | 0.1736 | 2.36 | 3.168e-05 | 1.976 | 6.24 | 2.336e-05 | 1.84 | 3*380/50 ACSR | 8 | [8 empty] | 0 | 0 | [7 empty] | 0.00035868 | 0.004876 | 0.015333 | 0.0040826 | 0.012893 | 0.011306 | 0.0038017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HPS12 | ND1 | HPS12 | ND1 | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 3*380/50 ACSR | 8 | NO C.T | NO C.T | 1800 | 685.872 | 1800 | 0.00035868 | 0.004876 | 0.015333 | 0.0040826 | 0.012893 | 0.011306 | 0.0038017 | 0.1736 | 2.36 | 3.168e-05 | 1.976 | 6.24 | 2.336e-05 | 1.84 | 3*380/50 ACSR | 8 | [8 empty] | 0 | 0 | [7 empty] | 0.00035868 | 0.004876 | 0.015333 | 0.0040826 | 0.012893 | 0.011306 | 0.0038017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بشاي | المصرية الامريكية | BSHAY | MSR-AMR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 0.35 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 2.9793e-05 | 0.00021839 | 0.00063017 | 7.9545e-05 | 0.00068698 | 0.00037776 | 0.00042665 | 0.01442 | 0.1057 | 1.302e-06 | 0.0385 | 0.3325 | 7.805e-07 | 0.2065 | 2*380/50 ACSR | 0.35 | [6 empty] | 619 | 620 | 0 | 0 | B_BSHI_EGAM_1 | BESHAI | EGYAMR |  |  |  |  | 2.9793e-05 | 0.00021839 | 0.00063017 | 7.9545e-05 | 0.00068698 | 0.00037776 | 0.00042665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بشاي | المصرية الامريكية | BSHAY | MSR-AMR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 0.35 | 1600/1 | 1200/1 | 1200 | 457.248 | 1200 | 2.9793e-05 | 0.00021839 | 0.00063017 | 7.9545e-05 | 0.00068698 | 0.00037776 | 0.00042665 | 0.01442 | 0.1057 | 1.302e-06 | 0.0385 | 0.3325 | 7.805e-07 | 0.2065 | 2*380/50 ACSR | 0.35 | [6 empty] | 619 | 620 | 0 | 0 | B_BSHI_EGAM_2 | BESHAI | EGYAMR |  |  |  |  | 2.9793e-05 | 0.00021839 | 0.00063017 | 7.9545e-05 | 0.00068698 | 0.00037776 | 0.00042665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النوبارية | بشاي | NOBARIA | BSHAY | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 51 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 2.1012 | 15.402 | 0.00018972 | 5.61 | 48.45 | 0.00011373 | 30.09 | 2*380/50 ACSR | 51 | [6 empty] | 618 | 619 | 0 | 0 | B_BSHI_NBRI_1 | NOBARIA | BESHAI |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النوبارية | بشاي | NOBARIA | BSHAY | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 51 | 2000/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 2.1012 | 15.402 | 0.00018972 | 5.61 | 48.45 | 0.00011373 | 30.09 | 2*380/50 ACSR | 51 | [6 empty] | 618 | 619 | 0 | 0 | B_BSHI_NBRI_2 | NOBARIA | BESHAI |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حوش عيسى | ابو قير | HOSHESA | ABO.KIR | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*405 AAAC 2*380/50 ACSR | 57.2 | 2500/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0054587 | 0.035962 | 0.095526 | 0.014355 | 0.10414 | 0.061737 | 0.069727 | 2.642 | 17.4056 | 0.00019737 | 6.948 | 50.404 | 0.00012756 | 33.748 | 2*405 AAAC | 32.8 | 2*380/50 ACSR | 24.4 |  |  |  |  | 649 | 650 | 0 | 0 |  | HOSH_ESA | ABKIR_1 |  |  |  |  | 0.0033817 | 0.020737 | 0.051594 | 0.0088099 | 0.056248 | 0.035402 | 0.039983 | 0.002077 | 0.015225 | 0.043932 | 0.0055455 | 0.047893 | 0.026335 | 0.029744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حوش عيسى | ابو قير | HOSHESA | ABO.KIR | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*405 AAAC 2*380/50 ACSR | 57.2 | 2500/1 | 1200/1 | 1150 | 438.196 | 1150 | 0.0054587 | 0.035962 | 0.095526 | 0.014355 | 0.10414 | 0.061737 | 0.069727 | 2.642 | 17.4056 | 0.00019737 | 6.948 | 50.404 | 0.00012756 | 33.748 | 2*405 AAAC | 32.8 | 2*380/50 ACSR | 24.4 |  |  |  |  | 649 | 650 | 0 | 0 |  | HOSH_ESA | ABKIR_1 |  |  |  |  | 0.0033817 | 0.020737 | 0.051594 | 0.0088099 | 0.056248 | 0.035402 | 0.039983 | 0.002077 | 0.015225 | 0.043932 | 0.0055455 | 0.047893 | 0.026335 | 0.029744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | حوش عيسى | ETY-BARD | HOSHESA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 30.5 | 1600/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 1.2566 | 9.211 | 0.00011346 | 3.355 | 28.975 | 6.8015e-05 | 17.995 | 2*380/50 ACSR | 30.5 | [6 empty] | 611 | 649 | 0 | 0 |  | ETAYBARD | HOSH_ESA |  |  |  |  | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ايتاي | حوش عيسى | ETY-BARD | HOSHESA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 30.5 | 1600/1 | 2500/1 | 1200 | 457.248 | 1200 | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 1.2566 | 9.211 | 0.00011346 | 3.355 | 28.975 | 6.8015e-05 | 17.995 | 2*380/50 ACSR | 30.5 | [6 empty] | 611 | 649 | 0 | 0 |  | ETAYBARD | HOSH_ESA |  |  |  |  | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع ابو المطامير | الغزل | EXT.A.MTMR | GHAZL | الاسكندرية وغرب الدلتا | Circuit & Cable | 1 | 220 | 1*380/50 ACSR XLPE 2000mm2 Elswedy energy | 32.3 | 2500/1 | 800/5 | 650 | 247.676 | 670 | 0.0053535 | 0.025976 | 0.094939 | 0.019567 | 0.060652 | 0.076803 | 0.037545 | 2.5911 | 12.5725 | 0.00019615 | 9.4706 | 29.3555 | 0.00015868 | 18.172 | 1*380/50 ACSR | 30.8 | XLPE 2000mm2 Elswedy energy | 1.5 |  |  |  |  | 629 | 652 | 0 | 0 | B_MATR5_TXTL_1 | MATMR500 | TEXTILE |  |  |  |  | 0.0053136 | 0.025455 | 0.042486 | 0.019091 | 0.060455 | 0.033243 | 0.037545 | 3.9886e-05 | 0.00052175 | 0.052454 | 0.00047647 | 0.00019742 | 0.04356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توسيع ابو المطامير | الغزل | EXT.A.MTMR | GHAZL | الاسكندرية وغرب الدلتا | Circuit & Cable | 2 | 220 | 1*380/50 ACSR XLPE 2000mm2 Elswedy energy | 32.3 | 2500/1 | 800/5 | 650 | 247.676 | 670 | 0.0053535 | 0.025976 | 0.094939 | 0.019567 | 0.060652 | 0.076803 | 0.037545 | 2.5911 | 12.5725 | 0.00019615 | 9.4706 | 29.3555 | 0.00015868 | 18.172 | 1*380/50 ACSR | 30.8 | XLPE 2000mm2 Elswedy energy | 1.5 |  |  |  |  | 629 | 652 | 0 | 0 | B_MATR5_TXTL_2 | MATMR500 | TEXTILE |  |  |  |  | 0.0053136 | 0.025455 | 0.042486 | 0.019091 | 0.060455 | 0.033243 | 0.037545 | 3.9886e-05 | 0.00052175 | 0.052454 | 0.00047647 | 0.00019742 | 0.04356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو المطامير | توسيع ابو المطامير | A.MATAMR | EXT.A.MTMR | الاسكندرية وغرب الدلتا | Cable | 1 | 220 | 2*XLPE 1600mm2 Elswedy (every circuit two cable in parralel) | 0.045 | 2500/1 | 3000/1 | 2400 | 914.496 | 2400 | 5.625e-07 | 5.6482e-06 | 0.0019166 | 9.5486e-06 | 3.3192e-06 | 0.0023087 | 0 | 0.00027225 | 0.0027337 | 3.96e-06 | 0.0046215 | 0.0016065 | 4.77e-06 | 0 | 2*XLPE 1600mm2 Elswedy (every circuit two cable in parralel) | 0.045 | [6 empty] | 628 | 629 | 0 | 0 | B_TMAT_MTMR5_1 | MATMR500 | TMTAMIR |  |  |  |  | 5.625e-07 | 5.6482e-06 | 0.0019166 | 9.5486e-06 | 3.3192e-06 | 0.0023087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابو المطامير | توسيع ابو المطامير | A.MATAMR | EXT.A.MTMR | الاسكندرية وغرب الدلتا | Cable | 2 | 220 | 2*XLPE 1600mm2 Elswedy (every circuit two cable in parralel) | 0.045 | 2500/1 | 3000/1 | 2400 | 914.496 | 2400 | 5.625e-07 | 5.6482e-06 | 0.0019166 | 9.5486e-06 | 3.3192e-06 | 0.0023087 | 0 | 0.00027225 | 0.0027337 | 3.96e-06 | 0.0046215 | 0.0016065 | 4.77e-06 | 0 | 2*XLPE 1600mm2 Elswedy (every circuit two cable in parralel) | 0.045 | [6 empty] | 628 | 629 | 0 | 0 | B_TMAT_MTMR5_2 | MATMR500 | TMTAMIR |  |  |  |  | 5.625e-07 | 5.6482e-06 | 0.0019166 | 9.5486e-06 | 3.3192e-06 | 0.0023087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | النوبارية | MENOUF | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 42.1 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0035837 | 0.026269 | 0.0758 | 0.0095682 | 0.082634 | 0.045439 | 0.05132 | 1.7345 | 12.7142 | 0.00015661 | 4.631 | 39.995 | 9.3883e-05 | 24.839 | 2*380/50 ACSR | 42.1 | [6 empty] | 526 | 618 | 0 | 0 | B_MNOF_NBRI_1 | MENOUF | NOBARIA |  |  |  |  | 0.0035837 | 0.026269 | 0.0758 | 0.0095682 | 0.082634 | 0.045439 | 0.05132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
منوف | النوبارية | MENOUF | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 42.1 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0035837 | 0.026269 | 0.0758 | 0.0095682 | 0.082634 | 0.045439 | 0.05132 | 1.7345 | 12.7142 | 0.00015661 | 4.631 | 39.995 | 9.3883e-05 | 24.839 | 2*380/50 ACSR | 42.1 | [6 empty] | 526 | 618 | 0 | 0 | B_MNOF_NBRI_2 | MENOUF | NOBARIA |  |  |  |  | 0.0035837 | 0.026269 | 0.0758 | 0.0095682 | 0.082634 | 0.045439 | 0.05132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العطف | المحمودية | AL-ATF | MAHMODIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 1.3 | 2000/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.00011066 | 0.00081116 | 0.0023406 | 0.00029545 | 0.0025517 | 0.0014031 | 0.0015847 | 0.05356 | 0.3926 | 4.836e-06 | 0.143 | 1.235 | 2.899e-06 | 0.767 | 2*380/50 ACSR | 1.3 | [6 empty] | 600 | 601 | 0 | 0 | B_ATTF_MHMD_1 | AL_ATTF | MHMOUDIA |  |  |  |  | 0.00011066 | 0.00081116 | 0.0023406 | 0.00029545 | 0.0025517 | 0.0014031 | 0.0015847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
العطف | المحمودية | AL-ATF | MAHMODIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 1.3 | 2000/1 | 1200/1 | 1200 | 457.248 | 1200 | 0.00011066 | 0.00081116 | 0.0023406 | 0.00029545 | 0.0025517 | 0.0014031 | 0.0015847 | 0.05356 | 0.3926 | 4.836e-06 | 0.143 | 1.235 | 2.899e-06 | 0.767 | 2*380/50 ACSR | 1.3 | [6 empty] | 600 | 601 | 0 | 0 | B_ATTF_MHMD_2 | AL_ATTF | MHMOUDIA |  |  |  |  | 0.00011066 | 0.00081116 | 0.0023406 | 0.00029545 | 0.0025517 | 0.0014031 | 0.0015847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سيدي سالم | العطف | SIDI-SALM | AL-ATF | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 42.8 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0036433 | 0.026706 | 0.077061 | 0.0097273 | 0.084008 | 0.046195 | 0.052174 | 1.7634 | 12.9256 | 0.00015922 | 4.708 | 40.66 | 9.5444e-05 | 25.252 | 2*380/50 ACSR | 42.8 | [6 empty] | 516 | 600 | 0 | 0 | B_ATTF_SALM_1 | SEDISALM | AL_ATTF |  |  |  |  | 0.0036433 | 0.026706 | 0.077061 | 0.0097273 | 0.084008 | 0.046195 | 0.052174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سيدي سالم | العطف | SIDI-SALM | AL-ATF | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 42.8 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0036433 | 0.026706 | 0.077061 | 0.0097273 | 0.084008 | 0.046195 | 0.052174 | 1.7634 | 12.9256 | 0.00015922 | 4.708 | 40.66 | 9.5444e-05 | 25.252 | 2*380/50 ACSR | 42.8 | [6 empty] | 516 | 600 | 0 | 0 | B_ATTF_SALM_2 | SEDISALM | AL_ATTF |  |  |  |  | 0.0036433 | 0.026706 | 0.077061 | 0.0097273 | 0.084008 | 0.046195 | 0.052174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | العطف | KAFR.ZYAIT | AL-ATF | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 60 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 2.472 | 18.12 | 0.0002232 | 6.6 | 57 | 0.0001338 | 35.4 | 2*380/50 ACSR | 60 | [6 empty] | 530 | 600 | 0 | 0 | B_ATTF_KZ20_1 | KFZYT220 | AL_ATTF |  |  |  |  | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كفر الزيات | العطف | KAFR.ZYAIT | AL-ATF | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 60 | 1600/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 2.472 | 18.12 | 0.0002232 | 6.6 | 57 | 0.0001338 | 35.4 | 2*380/50 ACSR | 60 | [6 empty] | 530 | 600 | 0 | 0 | B_ATTF_KZ20_2 | KFZYT220 | AL_ATTF |  |  |  |  | 0.0051074 | 0.037438 | 0.10803 | 0.013636 | 0.11777 | 0.064759 | 0.07314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب طنطا | النوبارية | SOTH.TANTA | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 52.75 | 2000/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0044903 | 0.032914 | 0.094975 | 0.011989 | 0.10354 | 0.056934 | 0.064303 | 2.1733 | 15.9305 | 0.00019623 | 5.8025 | 50.1125 | 0.00011763 | 31.1225 | 2*380/50 ACSR | 52.75 | [6 empty] | 527 | 618 | 0 | 0 | B_NBRI_TNTAS_1 | TANTA_S | NOBARIA |  |  |  |  | 0.0044903 | 0.032914 | 0.094975 | 0.011989 | 0.10354 | 0.056934 | 0.064303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب طنطا | النوبارية | SOTH.TANTA | NOBARIA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 52.75 | 2000/1 | 2000/1 | 1200 | 457.248 | 1200 | 0.0044903 | 0.032914 | 0.094975 | 0.011989 | 0.10354 | 0.056934 | 0.064303 | 2.1733 | 15.9305 | 0.00019623 | 5.8025 | 50.1125 | 0.00011763 | 31.1225 | 2*380/50 ACSR | 52.75 | [6 empty] | 527 | 618 | 0 | 0 | B_NBRI_TNTAS_2 | TANTA_S | NOBARIA |  |  |  |  | 0.0044903 | 0.032914 | 0.094975 | 0.011989 | 0.10354 | 0.056934 | 0.064303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | جنوب طنطا | TANTA | SOTH.TANTA | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | 2*380/50 ACSR | 10.41 | 1200/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.00088614 | 0.0064955 | 0.018743 | 0.0023659 | 0.020433 | 0.011236 | 0.01269 | 0.42889 | 3.1438 | 3.8725e-05 | 1.1451 | 9.8895 | 2.3214e-05 | 6.1419 | 2*380/50 ACSR | 10.41 | [6 empty] | 520 | 527 | 0 | 0 | B_TNTA_TNTAS_1 | TANTA | TANTA_S |  |  |  |  | 0.00088614 | 0.0064955 | 0.018743 | 0.0023659 | 0.020433 | 0.011236 | 0.01269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طنطا | جنوب طنطا | TANTA | SOTH.TANTA | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | 2*380/50 ACSR | 10.41 | 1200/1 | 2000/1 | 1000 | 381.04 | 1200 | 0.00088614 | 0.0064955 | 0.018743 | 0.0023659 | 0.020433 | 0.011236 | 0.01269 | 0.42889 | 3.1438 | 3.8725e-05 | 1.1451 | 9.8895 | 2.3214e-05 | 6.1419 | 2*380/50 ACSR | 10.41 | [6 empty] | 520 | 527 | 0 | 0 | B_TNTA_TNTAS_2 | TANTA | TANTA_S |  |  |  |  | 0.00088614 | 0.0064955 | 0.018743 | 0.0023659 | 0.020433 | 0.011236 | 0.01269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | ابوغالب | NRTH-GIZA | ABO.GHALEB | الاسكندرية وغرب الدلتا | Cable | 1 | 220 | XLPE 1200mm2 | 2.65 | 1600/1 | 1600/1 | 1000 | 381.04 | 1000 | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0.041605 | 0.52894 | 0.0001643 | 0.5353 | 0.1855 | 0.0001378 | 0 | XLPE 1200mm2 | 2.65 | [6 empty] | 401 | 627 | 0 | 0 | B_GHALB_GNTH_1 | GIZANRTH | ABUGHALB |  |  |  |  | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | ابوغالب | NRTH-GIZA | ABO.GHALEB | الاسكندرية وغرب الدلتا | Cable | 2 | 220 | XLPE 1200mm2 | 2.65 | 1600/1 | 1600/1 | 1000 | 381.04 | 1000 | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0.041605 | 0.52894 | 0.0001643 | 0.5353 | 0.1855 | 0.0001378 | 0 | XLPE 1200mm2 | 2.65 | [6 empty] | 401 | 627 | 0 | 0 | B_GHALB_GNTH_2 | GIZANRTH | ABUGHALB |  |  |  |  | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | ابوغالب | NRTH-GIZA | ABO.GHALEB | الاسكندرية وغرب الدلتا | Cable | 3 | 220 | XLPE 1200mm2 | 2.65 | 1600/1 | 1600/1 | 1000 | 381.04 | 1000 | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0.041605 | 0.52894 | 0.0001643 | 0.5353 | 0.1855 | 0.0001378 | 0 | XLPE 1200mm2 | 2.65 | [6 empty] | 401 | 627 | 0 | 0 | B_GHALB_GNTH_3 | GIZANRTH | ABUGHALB |  |  |  |  | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شمال الجيزة | ابوغالب | NRTH-GIZA | ABO.GHALEB | الاسكندرية وغرب الدلتا | Cable | 4 | 220 | XLPE 1200mm2 | 2.65 | 1600/1 | 1600/1 | 1000 | 381.04 | 1000 | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0.041605 | 0.52894 | 0.0001643 | 0.5353 | 0.1855 | 0.0001378 | 0 | XLPE 1200mm2 | 2.65 | [6 empty] | 401 | 627 | 0 | 0 | B_GHALB_GNTH_4 | GIZANRTH | ABUGHALB |  |  |  |  | 8.5961e-05 | 0.0010929 | 0.079521 | 0.001106 | 0.00038326 | 0.066695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السادات | ابوغالب | SADAT | ABO.GHALEB | الاسكندرية وغرب الدلتا | Circuit | 1 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR | 47 | 1600/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0096909 | 0.040247 | 0.064078 | 0.028537 | 0.11819 | 0.0418 | 0.07178 | 4.6904 | 19.4795 | 0.00013239 | 13.8121 | 57.2033 | 8.6365e-05 | 34.7417 | Thermal Invar 1*255/88 | 37.743 | 2*380/50 ACSR | 9.257 |  |  |  |  | 626 | 627 | 0 | 0 | B_GHLAB_SDAT_1 | SADAT | ABUGHALB |  |  |  |  | 0.0089029 | 0.034471 | 0.047411 | 0.026433 | 0.10002 | 0.031809 | 0.060496 | 0.00078799 | 0.0057761 | 0.016667 | 0.0021039 | 0.01817 | 0.0099913 | 0.011284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السادات | ابوغالب | SADAT | ABO.GHALEB | الاسكندرية وغرب الدلتا | Circuit | 2 | 220 | Thermal Invar 1*255/88 2*380/50 ACSR | 47 | 1600/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.0096909 | 0.040247 | 0.064078 | 0.028537 | 0.11819 | 0.0418 | 0.07178 | 4.6904 | 19.4795 | 0.00013239 | 13.8121 | 57.2033 | 8.6365e-05 | 34.7417 | Thermal Invar 1*255/88 | 37.743 | 2*380/50 ACSR | 9.257 |  |  |  |  | 626 | 627 | 0 | 0 | B_GHALB_SDAT_2 | SADAT | ABUGHALB |  |  |  |  | 0.0089029 | 0.034471 | 0.047411 | 0.026433 | 0.10002 | 0.031809 | 0.060496 | 0.00078799 | 0.0057761 | 0.016667 | 0.0021039 | 0.01817 | 0.0099913 | 0.011284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات (2و3) | الكريمات 1 | KURAIMAT2&3 | KURAIMAT-I | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 0.15 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 1.2769e-05 | 9.3595e-05 | 0.00027007 | 3.4091e-05 | 0.00029442 | 0.0001619 | 0.00018285 | 0.00618 | 0.0453 | 5.58e-07 | 0.0165 | 0.1425 | 3.345e-07 | 0.0885 | 2*380/50 ACSR | 0.15 | [6 empty] | 218 | 220 | 0 | 0 | B_KRIM_KRM2_2 | KURIMAT2 | KORIMAT |  |  |  |  | 1.2769e-05 | 9.3595e-05 | 0.00027007 | 3.4091e-05 | 0.00029442 | 0.0001619 | 0.00018285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب الفيوم | دمو | WEST-FAYUM | DEMO | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 36 | 1600/1 | 1200/5 | 1200 | 457.248 | 1340 | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 1.4832 | 10.872 | 0.00013392 | 3.96 | 34.2 | 8.028e-05 | 21.24 | 2*380/50 ACSR | 36 | [6 empty] | 212 | 216 | 0 | 0 | B_DEMO_WFYM_1 | WSTFAUOM | DEMO |  |  |  |  | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب الفيوم | دمو | WEST-FAYUM | DEMO | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 36 | 1600/1 | 1200/5 | 1200 | 457.248 | 1340 | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 1.4832 | 10.872 | 0.00013392 | 3.96 | 34.2 | 8.028e-05 | 21.24 | 2*380/50 ACSR | 36 | [6 empty] | 212 | 216 | 0 | 0 | B_DEMO_WFYM_2 | WSTFAUOM | DEMO |  |  |  |  | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوطرطور | البلاط | A.TARTOR | BALAT | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 115 | 600/1 | 1600/1 | 600 | 228.624 | 1340 | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 4.738 | 34.73 | 0.0004278 | 12.65 | 109.25 | 0.00025645 | 67.85 | 2*380/50 ACSR | 115 | [6 empty] | 224 | 225 | 0 | 0 | B_ATRT_BLAT_1 | ABUTRTOR | BALATT |  |  |  |  | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ابوطرطور | البلاط | A.TARTOR | BALAT | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 115 | 600/1 | 1600/1 | 600 | 228.624 | 1340 | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 4.738 | 34.73 | 0.0004278 | 12.65 | 109.25 | 0.00025645 | 67.85 | 2*380/50 ACSR | 115 | [6 empty] | 224 | 225 | 0 | 0 | B_ATRT_BLAT_2 | ABUTRTOR | BALATT |  |  |  |  | 0.0097893 | 0.071756 | 0.20706 | 0.026136 | 0.22572 | 0.12412 | 0.14019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | العوينات الجديدة | EST-OYNAT | NEW-OYNAT | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 65 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0055331 | 0.040558 | 0.11703 | 0.014773 | 0.12758 | 0.070156 | 0.079236 | 2.678 | 19.63 | 0.0002418 | 7.15 | 61.75 | 0.00014495 | 38.35 | 2*380/50 ACSR | 65 | [6 empty] | 101 | 132 | 0 | 0 |  | AWINAT | N_AWINAT |  |  |  |  | 0.0055331 | 0.040558 | 0.11703 | 0.014773 | 0.12758 | 0.070156 | 0.079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | العوينات الجديدة | EST-OYNAT | NEW-OYNAT | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 65 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0055331 | 0.040558 | 0.11703 | 0.014773 | 0.12758 | 0.070156 | 0.079236 | 2.678 | 19.63 | 0.0002418 | 7.15 | 61.75 | 0.00014495 | 38.35 | 2*380/50 ACSR | 65 | [6 empty] | 101 | 132 | 0 | 0 |  | AWINAT | N_AWINAT |  |  |  |  | 0.0055331 | 0.040558 | 0.11703 | 0.014773 | 0.12758 | 0.070156 | 0.079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | البلاط | EST-OYNAT | BALAT | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 384 | 1600/1 | 1600/1 | 1200 | 457.248 | 1340 | 0.032688 | 0.2396 | 0.69138 | 0.087273 | 0.75372 | 0.41446 | 0.4681 | 15.8208 | 115.968 | 0.0014285 | 42.24 | 364.8 | 0.00085632 | 226.56 | 2*380/50 ACSR | 384 | [6 empty] | 101 | 225 | -0.25 | -0.25 | B_AWNT_BLAT_1 | AWINAT | BALATT |  | الجزء الخاص بخطوط اسيوط بمنطقة مصر الوسطى طوله 289 كم + الجزء الخاص بخطوط اسوان بمنطقة مصر العليا طوله 95 كم |  |  | 0.032688 | 0.2396 | 0.69138 | 0.087273 | 0.75372 | 0.41446 | 0.4681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | البلاط | EST-OYNAT | BALAT | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 384 | 1600/1 | 1600/1 | 1200 | 457.248 | 1340 | 0.032688 | 0.2396 | 0.69138 | 0.087273 | 0.75372 | 0.41446 | 0.4681 | 15.8208 | 115.968 | 0.0014285 | 42.24 | 364.8 | 0.00085632 | 226.56 | 2*380/50 ACSR | 384 | [6 empty] | 101 | 225 | -0.25 | -0.25 | B_AWNT_BLAT_2 | AWINAT | BALATT |  | الجزء الخاص بخطوط اسيوط بمنطقة مصر الوسطى طوله 289 كم + الجزء الخاص بخطوط اسوان بمنطقة مصر العليا طوله 95 كم |  |  | 0.032688 | 0.2396 | 0.69138 | 0.087273 | 0.75372 | 0.41446 | 0.4681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | غرب مغاغة | SAMALUT | MAGAGA-WST | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 51 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 2.1012 | 15.402 | 0.00018972 | 5.61 | 48.45 | 0.00011373 | 30.09 | 2*380/50 ACSR | 51 | [6 empty] | 208 | 210 | 0 | 0 | B_MAGH_SML5_1 | SMLUT500 | MAGHAGHA |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | غرب مغاغة | SAMALUT | MAGAGA-WST | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 51 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 2.1012 | 15.402 | 0.00018972 | 5.61 | 48.45 | 0.00011373 | 30.09 | 2*380/50 ACSR | 51 | [6 empty] | 208 | 210 | 0 | 0 | B_MAGH_SML5_2 | SMLUT500 | MAGHAGHA |  |  |  |  | 0.0043413 | 0.031822 | 0.091824 | 0.011591 | 0.1001 | 0.055045 | 0.062169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمو | الكريمات (2و3) | DEMO | KURAIMAT2&3 | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 41 | 1200/5 | 1600/1 | 1200 | 457.248 | 1340 | 0.0034901 | 0.025583 | 0.07382 | 0.0093182 | 0.080475 | 0.044252 | 0.049979 | 1.6892 | 12.382 | 0.00015252 | 4.51 | 38.95 | 9.143e-05 | 24.19 | 2*380/50 ACSR | 41 | [6 empty] | 216 | 218 | 0 | 0 | B_DEMO_KRM2_1 | DEMO | KURIMAT2 |  |  |  |  | 0.0034901 | 0.025583 | 0.07382 | 0.0093182 | 0.080475 | 0.044252 | 0.049979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
دمو | الكريمات (2و3) | DEMO | KURAIMAT2&3 | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 41 | 1200/5 | 1600/1 | 1200 | 457.248 | 1340 | 0.0034901 | 0.025583 | 0.07382 | 0.0093182 | 0.080475 | 0.044252 | 0.049979 | 1.6892 | 12.382 | 0.00015252 | 4.51 | 38.95 | 9.143e-05 | 24.19 | 2*380/50 ACSR | 41 | [6 empty] | 216 | 218 | 0 | 0 | B_DEMO_KRM2_2 | DEMO | KURIMAT2 |  |  |  |  | 0.0034901 | 0.025583 | 0.07382 | 0.0093182 | 0.080475 | 0.044252 | 0.049979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف شرق | الكريمات (2و3) | BINSWF-EAST | KURAIMAT2&3 | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 27.3 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0023239 | 0.017034 | 0.049153 | 0.0062045 | 0.053585 | 0.029465 | 0.033279 | 1.1248 | 8.2446 | 0.00010156 | 3.003 | 25.935 | 6.0879e-05 | 16.107 | 2*380/50 ACSR | 27.3 | [6 empty] | 214 | 218 | 0 | 0 | B_BSFE_KRM2_1 | BSUEFEST | KURIMAT2 |  |  |  |  | 0.0023239 | 0.017034 | 0.049153 | 0.0062045 | 0.053585 | 0.029465 | 0.033279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف شرق | الكريمات (2و3) | BINSWF-EAST | KURAIMAT2&3 | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 27.3 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0023239 | 0.017034 | 0.049153 | 0.0062045 | 0.053585 | 0.029465 | 0.033279 | 1.1248 | 8.2446 | 0.00010156 | 3.003 | 25.935 | 6.0879e-05 | 16.107 | 2*380/50 ACSR | 27.3 | [6 empty] | 214 | 218 | 0 | 0 | B_BSFE_KRM2_2 | BSUEFEST | KURIMAT2 |  |  |  |  | 0.0023239 | 0.017034 | 0.049153 | 0.0062045 | 0.053585 | 0.029465 | 0.033279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | الوليدية | ASSYUT | WALIDIA | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 20 | 1200/1 | 1250/1 | 900 | 342.936 | 1340 | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0.824 | 6.04 | 7.44e-05 | 2.2 | 19 | 4.46e-05 | 11.8 | 2*380/50 ACSR | 20 | [6 empty] | 202 | 204 | 0 | 0 | B_AS50_WLDIA_3 | ASSUT500 | WALIDIA |  | محول التيار عند الوليدية لكل الدوائر 220 هي 1250 للقياس و 2000 للوقاية . اشارة من قطاعات الانتاج والمشرف على قطاع الوليدية بوجود تقادم للمعدات وان اقصى تحميل هو 900 امبير |  |  | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | الوليدية | ASSYUT | WALIDIA | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 20 | 1200/1 | 1250/1 | 900 | 342.936 | 1340 | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0.824 | 6.04 | 7.44e-05 | 2.2 | 19 | 4.46e-05 | 11.8 | 2*380/50 ACSR | 20 | [6 empty] | 202 | 204 | 0 | 0 | B_AS50_WLDIA_4 | ASSUT500 | WALIDIA |  | محول التيار عند الوليدية لكل الدوائر 220 هي 1250 للقياس و 2000 للوقاية . اشارة من قطاعات الانتاج والمشرف على قطاع الوليدية بوجود تقادم للمعدات وان اقصى تحميل هو 900 امبير |  |  | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب اسيوط | اسيوط 500 | WST.ASSYUT | ASSYUT | مصر الوسطي | Circuit & Cable | 1 | 220 | XLPE 1600mm2 Elswedy 2*380/50 ACSR | 5.2 | 2000/1 | 1200/1 | 1200 | 457.248 | 1340 | 0.00031037 | 0.0024242 | 0.052253 | 0.0016155 | 0.006213 | 0.059672 | 0.003657 | 0.15022 | 1.1733 | 0.00010796 | 0.78188 | 3.0071 | 0.00012329 | 1.77 | XLPE 1600mm2 Elswedy | 2.2 | 2*380/50 ACSR | 3 |  |  |  |  | 201 | 202 | 0 | 0 | B_AS50_WASUT_1 | N_ASSUTG | ASSUT500 |  | يوجد كابل 1*1200 بين الخلية و الدائرة وهي تتحمل 950 امبير من ناحية محطة غرب اسيوط طولها 90 متر . اشارة من قطاع الوقاية بمصر الوسطى انه تم ضبط انذار جهاز overload على 1000 امبير والفصل على 1200 امبير من الجهتين ورقم الملف 19 . |  |  | 5.5e-05 | 0.00055227 | 0.046851 | 0.00093364 | 0.00032455 | 0.056434 | 0 | 0.00025537 | 0.0018719 | 0.0054014 | 0.00068182 | 0.0058884 | 0.003238 | 0.003657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب اسيوط | اسيوط 500 | WST.ASSYUT | ASSYUT | مصر الوسطي | Circuit & Cable | 2 | 220 | XLPE 1600mm2 Elswedy 2*380/50 ACSR | 5.2 | 2000/1 | 1200/1 | 1200 | 457.248 | 1340 | 0.00031037 | 0.0024242 | 0.052253 | 0.0016155 | 0.006213 | 0.059672 | 0.003657 | 0.15022 | 1.1733 | 0.00010796 | 0.78188 | 3.0071 | 0.00012329 | 1.77 | XLPE 1600mm2 Elswedy | 2.2 | 2*380/50 ACSR | 3 |  |  |  |  | 201 | 202 | 0 | 0 | B_AS50_WASUT_2 | N_ASSUTG | ASSUT500 |  |  |  |  | 5.5e-05 | 0.00055227 | 0.046851 | 0.00093364 | 0.00032455 | 0.056434 | 0 | 0.00025537 | 0.0018719 | 0.0054014 | 0.00068182 | 0.0058884 | 0.003238 | 0.003657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب اسيوط | الوليدية | WST.ASSYUT | WALIDIA | مصر الوسطي | Circuit & Cable | 1 | 220 | Thermal double 2*255/88 2*380/50 ACSR | 28.5 | 2000/1 | 1250/1 | 950 | 361.988 | 1200 | 0.0027081 | 0.018408 | 0.049854 | 0.0094992 | 0.059948 | 0.03021 | 0.038004 | 1.3107 | 8.9095 | 0.000103 | 4.5976 | 29.0146 | 6.2416e-05 | 18.3942 | Thermal double 2*255/88 | 8.5 | 2*380/50 ACSR | 20 |  |  |  |  | 201 | 204 | 0 | 0 | B_WASUT_WLD_1 | N_ASSUTG | WALIDIA |  | محول التيار عند الوليدية لكل دوائر 220 هي 1250 للقياس و 2000 للوقاية . يوجد كابل 1*1200 بين الخلية و الدائرة وهي تتحمل 950 امبير من ناحية محطة غرب اسيوط طولها 70 متر . محول التيار عند غرب اسيوط 1/1600 و عند الوليدية 1/1200 عند م فهمي |  |  | 0.0010056 | 0.0059287 | 0.013844 | 0.0049537 | 0.020691 | 0.0086231 | 0.013624 | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب اسيوط | الوليدية | WST.ASSYUT | WALIDIA | مصر الوسطي | Circuit & Cable | 2 | 220 | Thermal double 2*255/88 2*380/50 ACSR | 28.5 | 2000/1 | 1250/1 | 950 | 361.988 | 1200 | 0.0027081 | 0.018408 | 0.049854 | 0.0094992 | 0.059948 | 0.03021 | 0.038004 | 1.3107 | 8.9095 | 0.000103 | 4.5976 | 29.0146 | 6.2416e-05 | 18.3942 | Thermal double 2*255/88 | 8.5 | 2*380/50 ACSR | 20 |  |  |  |  | 201 | 204 | 0 | 0 | B_WASUT_WLD_2 | N_ASSUTG | WALIDIA |  |  |  |  | 0.0010056 | 0.0059287 | 0.013844 | 0.0049537 | 0.020691 | 0.0086231 | 0.013624 | 0.0017025 | 0.012479 | 0.03601 | 0.0045455 | 0.039256 | 0.021586 | 0.02438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ريفا | غرب اسيوط | RIVA | WST.ASSYUT | مصر الوسطي | Circuit | 1 | 220 | Thermal double 2*255/88 | 31.6 | 1600/1 | 2000/1 | 1300 | 495.352 | 1300 | 0.0037386 | 0.022041 | 0.051468 | 0.018416 | 0.076923 | 0.032058 | 0.05065 | 1.8095 | 10.6678 | 0.00010634 | 8.9134 | 37.2309 | 6.6235e-05 | 24.5148 | Thermal double 2*255/88 | 31.6 | [6 empty] | 200 | 201 | 0 | 0 | B_NASS_REFA_1 | REFFA1 | N_ASSUTG |  | يوجد كابل 1*2000 بين الخلية و الدائرة وهي تتحمل 1400 امبير من ناحية محطة غرب اسيوط طولها 70 متر وقد كان الكابل القديم 1*1200 |  |  | 0.0037386 | 0.022041 | 0.051468 | 0.018416 | 0.076923 | 0.032058 | 0.05065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ريفا | غرب اسيوط | RIVA | WST.ASSYUT | مصر الوسطي | Circuit | 2 | 220 | Thermal double 2*255/88 | 31.6 | 1600/1 | 2000/1 | 1300 | 495.352 | 1300 | 0.0037386 | 0.022041 | 0.051468 | 0.018416 | 0.076923 | 0.032058 | 0.05065 | 1.8095 | 10.6678 | 0.00010634 | 8.9134 | 37.2309 | 6.6235e-05 | 24.5148 | Thermal double 2*255/88 | 31.6 | [6 empty] | 200 | 201 | 0 | 0 | B_NASS_REFA_2 | REFFA1 | N_ASSUTG |  | يوجد كابل 1*2000 بين الخلية و الدائرة وهي تتحمل 1400 امبير من ناحية محطة غرب اسيوط طولها 70 متر وقد كان الكابل القديم 1*1201 |  |  | 0.0037386 | 0.022041 | 0.051468 | 0.018416 | 0.076923 | 0.032058 | 0.05065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طما | ريفا | TEMA | RIVA | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 50 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 2.06 | 15.1 | 0.000186 | 5.5 | 47.5 | 0.0001115 | 29.5 | 2*380/50 ACSR | 50 | [6 empty] | 130 | 200 | 0 | 0 | B_REF1_TEMA_1 | TEMA | REFFA1 |  |  |  |  | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طما | ريفا | TEMA | RIVA | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 50 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 2.06 | 15.1 | 0.000186 | 5.5 | 47.5 | 0.0001115 | 29.5 | 2*380/50 ACSR | 50 | [6 empty] | 130 | 200 | 0 | 0 | B_REF1_TEMA_2 | TEMA | REFFA1 |  |  |  |  | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | شرق اسيوط | MALAWI | EST.ASSUT | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 110 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0093636 | 0.068636 | 0.19805 | 0.025 | 0.21591 | 0.11873 | 0.13409 | 4.532 | 33.22 | 0.0004092 | 12.1 | 104.5 | 0.0002453 | 64.9 | 2*380/50 ACSR | 110 | [6 empty] | 206 | 207 | 0 | 0 | B_MLAW_ASUTE_1 | MLAWY | ASUT_EST |  |  |  |  | 0.0093636 | 0.068636 | 0.19805 | 0.025 | 0.21591 | 0.11873 | 0.13409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | شرق اسيوط | MALAWI | EST.ASSUT | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 110 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0093636 | 0.068636 | 0.19805 | 0.025 | 0.21591 | 0.11873 | 0.13409 | 4.532 | 33.22 | 0.0004092 | 12.1 | 104.5 | 0.0002453 | 64.9 | 2*380/50 ACSR | 110 | [6 empty] | 206 | 207 | 0 | 0 | B_MLAW_ASUTE_2 | MLAWY | ASUT_EST |  |  |  |  | 0.0093636 | 0.068636 | 0.19805 | 0.025 | 0.21591 | 0.11873 | 0.13409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القناة للسكر | ملوي | SUGR.CANAL | MALAWI | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 52.6 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0044775 | 0.032821 | 0.094705 | 0.011955 | 0.10324 | 0.056772 | 0.06412 | 2.1671 | 15.8852 | 0.00019567 | 5.786 | 49.97 | 0.0001173 | 31.034 | 2*380/50 ACSR | 52.6 | [6 empty] | 205 | 206 | 0 | 0 | B_MLAW_SOKR1 | CANA_SKR | MLAWY |  |  |  |  | 0.0044775 | 0.032821 | 0.094705 | 0.011955 | 0.10324 | 0.056772 | 0.06412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القناة للسكر | ملوي | SUGR.CANAL | MALAWI | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 52.6 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0044775 | 0.032821 | 0.094705 | 0.011955 | 0.10324 | 0.056772 | 0.06412 | 2.1671 | 15.8852 | 0.00019567 | 5.786 | 49.97 | 0.0001173 | 31.034 | 2*380/50 ACSR | 52.6 | [6 empty] | 205 | 206 | 0 | 0 | B_MLAW_SOKR2 | CANA_SKR | MLAWY |  |  |  |  | 0.0044775 | 0.032821 | 0.094705 | 0.011955 | 0.10324 | 0.056772 | 0.06412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوليدية | شرق اسيوط | WALIDIA | EST.ASSUT | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 27 | 1250/1 | 2500/1 | 900 | 342.936 | 1200 | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 1.1124 | 8.154 | 0.00010044 | 2.97 | 25.65 | 6.021e-05 | 15.93 | 2*380/50 ACSR | 27 | [6 empty] | 204 | 207 | 0 | 0 | B_WALD_ASUTE_1 | WALIDIA | ASUT_EST |  | محول التيار عند الوليدية لكل الدوائر 220 هي 1250 للقياس و 2000 للوقاية . اشارة من قطاعات الانتاج والمشرف على قطاع الوليدية بوجود تقادم للمعدات وان اقصى تحميل هو 900 امبير |  |  | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الوليدية | شرق اسيوط | WALIDIA | EST.ASSUT | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 27 | 1250/1 | 2500/1 | 900 | 342.936 | 1200 | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 1.1124 | 8.154 | 0.00010044 | 2.97 | 25.65 | 6.021e-05 | 15.93 | 2*380/50 ACSR | 27 | [6 empty] | 204 | 207 | 0 | 0 | B_WALD_ASUTE_2 | WALIDIA | ASUT_EST |  | محول التيار عند الوليدية لكل الدوائر 220 هي 1250 للقياس و 2000 للوقاية . اشارة من قطاعات الانتاج والمشرف على قطاع الوليدية بوجود تقادم للمعدات وان اقصى تحميل هو 900 امبير |  |  | 0.0022983 | 0.016847 | 0.048613 | 0.0061364 | 0.052996 | 0.029142 | 0.032913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف الصناعية | الكوم الاحمر | INDS.BANISW | KOM.AHMAR | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 17 | 2500/1 | 1200/1 | 1340 | 510.5936 | 1340 | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0.7004 | 5.134 | 6.324e-05 | 1.87 | 16.15 | 3.791e-05 | 10.03 | 2*380/50 ACSR | 17 | [6 empty] | 217 | 219 | 0 | 0 | B_INDB_KAHMR_1 | IND_BNSF | KOM_AHMR |  |  |  |  | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف الصناعية | الكوم الاحمر | INDS.BANISW | KOM.AHMAR | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 17 | 2500/1 | 1200/1 | 1340 | 510.5936 | 1340 | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0.7004 | 5.134 | 6.324e-05 | 1.87 | 16.15 | 3.791e-05 | 10.03 | 2*380/50 ACSR | 17 | [6 empty] | 217 | 219 | 0 | 0 | B_INDB_KAHMR_2 | IND_BNSF | KOM_AHMR |  |  |  |  | 0.0014471 | 0.010607 | 0.030608 | 0.0038636 | 0.033368 | 0.018348 | 0.020723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب الفيوم | الكوم الاحمر | WEST-FAYUM | KOM.AHMAR | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 70.5 | 1600/1 | 1200/1 | 1340 | 510.5936 | 1340 | 0.0060012 | 0.04399 | 0.12693 | 0.016023 | 0.13838 | 0.076092 | 0.08594 | 2.9046 | 21.291 | 0.00026226 | 7.755 | 66.975 | 0.00015721 | 41.595 | 2*380/50 ACSR | 70.5 | [6 empty] | 212 | 219 | 0 | 0 | B_KAHMR_WFYOM1 | WSTFAUOM | KOM_AHMR |  |  |  |  | 0.0060012 | 0.04399 | 0.12693 | 0.016023 | 0.13838 | 0.076092 | 0.08594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب الفيوم | الكوم الاحمر | WEST-FAYUM | KOM.AHMAR | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 70.5 | 1600/1 | 1200/1 | 1340 | 510.5936 | 1340 | 0.0060012 | 0.04399 | 0.12693 | 0.016023 | 0.13838 | 0.076092 | 0.08594 | 2.9046 | 21.291 | 0.00026226 | 7.755 | 66.975 | 0.00015721 | 41.595 | 2*380/50 ACSR | 70.5 | [6 empty] | 212 | 219 | 0 | 0 | B_KAHMR_WFYOM2 | WSTFAUOM | KOM_AHMR |  |  |  |  | 0.0060012 | 0.04399 | 0.12693 | 0.016023 | 0.13838 | 0.076092 | 0.08594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مغاغة | غرب الفيوم | MAGAGA-WST | WEST-FAYUM | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 75.6 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0064354 | 0.047172 | 0.13612 | 0.017182 | 0.14839 | 0.081597 | 0.092157 | 3.1147 | 22.8312 | 0.00028123 | 8.316 | 71.82 | 0.00016859 | 44.604 | 2*380/50 ACSR | 75.6 | [6 empty] | 210 | 212 | 0 | 0 | B_MAGH_WFYM_1 | MAGHAGHA | WSTFAUOM |  |  |  |  | 0.0064354 | 0.047172 | 0.13612 | 0.017182 | 0.14839 | 0.081597 | 0.092157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مغاغة | غرب الفيوم | MAGAGA-WST | WEST-FAYUM | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 75.6 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0064354 | 0.047172 | 0.13612 | 0.017182 | 0.14839 | 0.081597 | 0.092157 | 3.1147 | 22.8312 | 0.00028123 | 8.316 | 71.82 | 0.00016859 | 44.604 | 2*380/50 ACSR | 75.6 | [6 empty] | 210 | 212 | 0 | 0 | B_MAGH_WFYM_2 | MAGHAGHA | WSTFAUOM |  |  |  |  | 0.0064354 | 0.047172 | 0.13612 | 0.017182 | 0.14839 | 0.081597 | 0.092157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات 1 | اللاهون | KURAIMAT-I | LAHON | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 19 | 1500/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0.7828 | 5.738 | 7.068e-05 | 2.09 | 18.05 | 4.237e-05 | 11.21 | 2*380/50 ACSR | 19 | [6 empty] | 220 | 223 | 0 | 0 | B_LAHON_KORMT1 | KORIMAT | EL_LAHON |  |  |  |  | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات 1 | اللاهون | KURAIMAT-I | LAHON | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 19 | 1500/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0.7828 | 5.738 | 7.068e-05 | 2.09 | 18.05 | 4.237e-05 | 11.21 | 2*380/50 ACSR | 19 | [6 empty] | 220 | 223 | 0 | 0 | B_LAHON_KORMT2 | KORIMAT | EL_LAHON |  |  |  |  | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طامية | اللاهون | TAMEIA | LAHON | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 31 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0026388 | 0.019343 | 0.055815 | 0.0070455 | 0.060847 | 0.033459 | 0.037789 | 1.2772 | 9.362 | 0.00011532 | 3.41 | 29.45 | 6.913e-05 | 18.29 | 2*380/50 ACSR | 31 | [6 empty] | 222 | 223 | 0 | 0 | B_TAMEA_LAHON1 | TAMEIA | EL_LAHON |  | محولات التيار في طامية 1/800/1600 امبير وتم اختيار 1600 امبير |  |  | 0.0026388 | 0.019343 | 0.055815 | 0.0070455 | 0.060847 | 0.033459 | 0.037789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طامية | اللاهون | TAMEIA | LAHON | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 31 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.0026388 | 0.019343 | 0.055815 | 0.0070455 | 0.060847 | 0.033459 | 0.037789 | 1.2772 | 9.362 | 0.00011532 | 3.41 | 29.45 | 6.913e-05 | 18.29 | 2*380/50 ACSR | 31 | [6 empty] | 222 | 223 | 0 | 0 | B_TAMEA_LAHON2 | TAMEIA | EL_LAHON |  | محولات التيار في طامية 1/800/1600 امبير وتم اختيار 1600 امبير |  |  | 0.0026388 | 0.019343 | 0.055815 | 0.0070455 | 0.060847 | 0.033459 | 0.037789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | طامية | HADAYEK.OCT | TAMEIA | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 485 | 222 | 0 | 0 | B_HDEK_TAMEA_1 | HDEK_OCT | TAMEIA |  | محولات التيار في طامية 1/800/1600 امبير وتم اختيار 1600 امبير |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | طامية | HADAYEK.OCT | TAMEIA | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 485 | 222 | 0 | 0 | B_HDEK_TAMEA_2 | HDEK_OCT | TAMEIA |  | محولات التيار في طامية 1/800/1600 امبير وتم اختيار 1600 امبير |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | اكتوبر | HADAYEK.OCT | 6-OCTOBR | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 14 | 1600/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0011917 | 0.0087355 | 0.025207 | 0.0031818 | 0.027479 | 0.01511 | 0.017066 | 0.5768 | 4.228 | 5.208e-05 | 1.54 | 13.3 | 3.122e-05 | 8.26 | 2*380/50 ACSR | 14 | [6 empty] | 485 | 410 | 0 | 0 | B_6_OC_HDEK_1 | HDEK_OCT | 6_OCTBR |  |  |  |  | 0.0011917 | 0.0087355 | 0.025207 | 0.0031818 | 0.027479 | 0.01511 | 0.017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | اكتوبر | HADAYEK.OCT | 6-OCTOBR | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR | 14 | 1600/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.0011917 | 0.0087355 | 0.025207 | 0.0031818 | 0.027479 | 0.01511 | 0.017066 | 0.5768 | 4.228 | 5.208e-05 | 1.54 | 13.3 | 3.122e-05 | 8.26 | 2*380/50 ACSR | 14 | [6 empty] | 485 | 410 | 0 | 0 | B_6_OC_HDEK_2 | HDEK_OCT | 6_OCTBR |  |  |  |  | 0.0011917 | 0.0087355 | 0.025207 | 0.0031818 | 0.027479 | 0.01511 | 0.017066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | اكتوبر | HADAYEK.OCT | 6-OCTOBR | القاهرة | Circuit | 3 | 220 | 2*380/50 ACSR | 16.67 | 1600/1 | 1250/1 | 1250 | 476.3 | 1340 | 0.001419 | 0.010402 | 0.030014 | 0.0037886 | 0.03272 | 0.017992 | 0.020321 | 0.6868 | 5.0343 | 6.2012e-05 | 1.8337 | 15.8365 | 3.7174e-05 | 9.8353 | 2*380/50 ACSR | 16.67 | [6 empty] | 485 | 410 | 0 | 0 | B_6OCT_HDEK_3 | HDEK_OCT | 6_OCTBR |  |  |  |  | 0.001419 | 0.010402 | 0.030014 | 0.0037886 | 0.03272 | 0.017992 | 0.020321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | الجمال | HADAYEK.OCT | ELGAMMAL | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 8.5 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.00072355 | 0.0053037 | 0.015304 | 0.0019318 | 0.016684 | 0.0091742 | 0.010362 | 0.3502 | 2.567 | 3.162e-05 | 0.935 | 8.075 | 1.8955e-05 | 5.015 | 2*380/50 ACSR | 8.5 | [6 empty] | 485 | 411 | 0 | 0 | B_ALGAM_HDEK_1 | HDEK_OCT | ALGAMAL |  |  |  |  | 0.00072355 | 0.0053037 | 0.015304 | 0.0019318 | 0.016684 | 0.0091742 | 0.010362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | الهضبة 1 | HADAYEK.OCT | HADABA-I | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 11 | 1600/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.00093636 | 0.0068636 | 0.019805 | 0.0025 | 0.021591 | 0.011873 | 0.013409 | 0.4532 | 3.322 | 4.092e-05 | 1.21 | 10.45 | 2.453e-05 | 6.49 | 2*380/50 ACSR | 11 | [6 empty] | 485 | 408 | 0 | 0 | B_HDEK_HDBA_1 | HDEK_OCT | HADABA |  | تم الاتصال بالمحطة وتبين ان محولات التيار من جهة حدائق اكتوبر 1/1600 |  |  | 0.00093636 | 0.0068636 | 0.019805 | 0.0025 | 0.021591 | 0.011873 | 0.013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حدائق اكتوبر | الهضبة 1 | HADAYEK.OCT | HADABA-I | القاهرة | Circuit | 2 | 220 | 2*380/50 ACSR | 11 | 1600/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.00093636 | 0.0068636 | 0.019805 | 0.0025 | 0.021591 | 0.011873 | 0.013409 | 0.4532 | 3.322 | 4.092e-05 | 1.21 | 10.45 | 2.453e-05 | 6.49 | 2*380/50 ACSR | 11 | [6 empty] | 485 | 408 | 0 | 0 | B_HDEK_HDBA_2 | HDEK_OCT | HADABA |  | تم الاتصال بالمحطة وتبين ان محولات التيار من جهة حدائق اكتوبر 1/1600 |  |  | 0.00093636 | 0.0068636 | 0.019805 | 0.0025 | 0.021591 | 0.011873 | 0.013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اكتوبر.6 | الجمال | 6-OCTOBR | ELGAMMAL | القاهرة | Circuit | 1 | 220 | 2*380/50 ACSR | 19 | 1250/1 | 1600/1 | 1250 | 476.3 | 1340 | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0.7828 | 5.738 | 7.068e-05 | 2.09 | 18.05 | 4.237e-05 | 11.21 | 2*380/50 ACSR | 19 | [6 empty] | 410 | 411 | 0 | 0 | B_ALGAMAL_6_OC | 6_OCTBR | ALGAMAL |  |  |  |  | 0.0016174 | 0.011855 | 0.034209 | 0.0043182 | 0.037293 | 0.020507 | 0.023161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | سمالوط | MALAWI | SAMALUT | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 70 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 2.884 | 21.14 | 0.0002604 | 7.7 | 66.5 | 0.0001561 | 41.3 | 2*380/50 ACSR | 70 | [6 empty] | 206 | 208 | 0 | 0 | B_MLAW_SML5_1 | MLAWY | SMLUT500 |  |  |  |  | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | سمالوط | MALAWI | SAMALUT | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 70 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 2.884 | 21.14 | 0.0002604 | 7.7 | 66.5 | 0.0001561 | 41.3 | 2*380/50 ACSR | 70 | [6 empty] | 206 | 208 | 0 | 0 | B_MLAW_SML5_2 | MLAWY | SMLUT500 |  |  |  |  | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | نجع حمادي الصناعية | SOTH-QUENA | Industrial_NAG-HAM | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 52 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0044264 | 0.032446 | 0.093625 | 0.011818 | 0.10207 | 0.056125 | 0.063388 | 2.1424 | 15.704 | 0.00019344 | 5.72 | 49.4 | 0.00011596 | 30.68 | 2*380/50 ACSR | 52 | [6 empty] | 118 |  | 0 | 0 |  | QENA | [5 empty] | 0.0044264 | 0.032446 | 0.093625 | 0.011818 | 0.10207 | 0.056125 | 0.063388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | نجع حمادي الصناعية | SOTH-QUENA | Industrial_NAG-HAM | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 52 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0044264 | 0.032446 | 0.093625 | 0.011818 | 0.10207 | 0.056125 | 0.063388 | 2.1424 | 15.704 | 0.00019344 | 5.72 | 49.4 | 0.00011596 | 30.68 | 2*380/50 ACSR | 52 | [6 empty] | 118 |  | 0 | 0 |  | QENA | [5 empty] | 0.0044264 | 0.032446 | 0.093625 | 0.011818 | 0.10207 | 0.056125 | 0.063388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | جرجا | NAG-HAM | GERGA | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 67 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0057033 | 0.041806 | 0.12063 | 0.015227 | 0.13151 | 0.072314 | 0.081674 | 2.7604 | 20.234 | 0.00024924 | 7.37 | 63.65 | 0.00014941 | 39.53 | 2*380/50 ACSR | 67 | [6 empty] | 120 | 128 | 0 | 0 | B_GRGA_NH50_1 | NHMDI500 | GERGA |  |  |  |  | 0.0057033 | 0.041806 | 0.12063 | 0.015227 | 0.13151 | 0.072314 | 0.081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | جرجا | NAG-HAM | GERGA | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 67 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0057033 | 0.041806 | 0.12063 | 0.015227 | 0.13151 | 0.072314 | 0.081674 | 2.7604 | 20.234 | 0.00024924 | 7.37 | 63.65 | 0.00014941 | 39.53 | 2*380/50 ACSR | 67 | [6 empty] | 120 | 128 | 0 | 0 | B_GRGA_NH50_2 | NHMDI500 | GERGA |  |  |  |  | 0.0057033 | 0.041806 | 0.12063 | 0.015227 | 0.13151 | 0.072314 | 0.081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 4 | بنبان 3 | BENBAN-4 | BENBAN-3 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 2 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0.0824 | 0.604 | 7.44e-06 | 0.22 | 1.9 | 4.46e-06 | 1.18 | 2*380/50 ACSR | 2 | [6 empty] | 115 | 119 | 0 | 0 | B_BEN3_BEN4_1 | BENBAN_4 | BENBAN_3 |  |  |  |  | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 4 | بنبان 3 | BENBAN-4 | BENBAN-3 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 2 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0.0824 | 0.604 | 7.44e-06 | 0.22 | 1.9 | 4.46e-06 | 1.18 | 2*380/50 ACSR | 2 | [6 empty] | 115 | 119 | 0 | 0 | B_BEN3_BEN4_2 | BENBAN_4 | BENBAN_3 |  |  |  |  | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 2 | بنبان 3 | BENBAN-2 | BENBAN-3 | مصر العليا | Circuit | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 2 | 1600/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.00014707 | 0.00141 | 0.0032635 | 0.00108 | 0.0042454 | 0.002271 | 0.00094513 | 0.071183 | 0.68246 | 6.7428e-06 | 0.52274 | 2.0548 | 4.6922e-06 | 0.45744 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 2 | [6 empty] | 111 | 119 | 0 | 0 | B_BEN2_BEN3_1 | BENBAN_2 | BENBAN_3 |  | محول تيار من الطرفين |  |  | 0.00014707 | 0.00141 | 0.0032635 | 0.00108 | 0.0042454 | 0.002271 | 0.00094513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 2 | بنبان 3 | BENBAN-2 | BENBAN-3 | مصر العليا | Circuit | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 2 | 1600/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.00014707 | 0.00141 | 0.0032635 | 0.00108 | 0.0042454 | 0.002271 | 0.00094513 | 0.071183 | 0.68246 | 6.7428e-06 | 0.52274 | 2.0548 | 4.6922e-06 | 0.45744 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 2 | [6 empty] | 111 | 119 | 0 | 0 | B_BEN2_BEN3_2 | BENBAN_2 | BENBAN_3 |  | محول تيار من الطرفين |  |  | 0.00014707 | 0.00141 | 0.0032635 | 0.00108 | 0.0042454 | 0.002271 | 0.00094513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 1 | بنبان 2 | BENBAN-1 | BENBAN-2 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 2 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0.0824 | 0.604 | 7.44e-06 | 0.22 | 1.9 | 4.46e-06 | 1.18 | 2*380/50 ACSR | 2 | [6 empty] | 109 | 111 | 0 | 0 | B_BEN1_BEN2_1 | BENBAN_1 | BENBAN_2 |  |  |  |  | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 1 | بنبان 2 | BENBAN-1 | BENBAN-2 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 2 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0.0824 | 0.604 | 7.44e-06 | 0.22 | 1.9 | 4.46e-06 | 1.18 | 2*380/50 ACSR | 2 | [6 empty] | 109 | 111 | 0 | 0 | B_BEN1_BEN2_2 | BENBAN_1 | BENBAN_2 |  |  |  |  | 0.00017025 | 0.0012479 | 0.003601 | 0.00045455 | 0.0039256 | 0.0021586 | 0.002438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | وادي النقرة | ASWAN-DAM | WAD.NOKRA | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 65.7 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0055926 | 0.040995 | 0.11829 | 0.014932 | 0.12896 | 0.070911 | 0.080089 | 2.7068 | 19.8414 | 0.0002444 | 7.227 | 62.415 | 0.00014651 | 38.763 | 2*380/50 ACSR | 65.7 | [6 empty] | 108 | 110 | 0 | 0 | B_ASW1_NKRA_1 | ASWNDAM1 | WADINKRA |  |  |  |  | 0.0055926 | 0.040995 | 0.11829 | 0.014932 | 0.12896 | 0.070911 | 0.080089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | وادي النقرة | ASWAN-DAM | WAD.NOKRA | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR THERMAL 2*357/54 ACSS/TW ,728kcmil | 65.7 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0051245 | 0.044269 | 0.11148 | 0.027567 | 0.13542 | 0.073182 | 0.049933 | 2.4802 | 21.4263 | 0.00023032 | 13.3422 | 65.5418 | 0.0001512 | 24.1674 | 2*380/50 ACSR | 25.3 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 40.4 |  |  |  |  | 108 | 110 | 0 | 0 | B_ASW1_NKRA_2 | ASWNDAM1 | WADINKRA |  |  |  |  | 0.0021536 | 0.015786 | 0.045552 | 0.00575 | 0.049659 | 0.027307 | 0.030841 | 0.0029708 | 0.028483 | 0.065923 | 0.021817 | 0.085758 | 0.045875 | 0.019092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النقرة | بنبان 4 | WAD.NOKRA | BENBAN-4 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR THERMAL 2*357/54 ACSS/TW ,728kcmil | 41.7 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0033596 | 0.027349 | 0.072313 | 0.014606 | 0.084472 | 0.045929 | 0.038591 | 1.6261 | 13.2368 | 0.00014941 | 7.0694 | 40.8843 | 9.4895e-05 | 18.678 | 2*380/50 ACSR | 25.3 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 16.4 |  |  |  |  | 110 | 115 | 0 | 0 | B_BEN4_NKRA_1 | WADINKRA | BENBAN_4 |  |  |  |  | 0.0021536 | 0.015786 | 0.045552 | 0.00575 | 0.049659 | 0.027307 | 0.030841 | 0.001206 | 0.011562 | 0.026761 | 0.0088563 | 0.034813 | 0.018623 | 0.0077501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
وادي النقرة | بنبان 4 | WAD.NOKRA | BENBAN-4 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 41.7 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0035497 | 0.026019 | 0.07508 | 0.0094773 | 0.081849 | 0.045008 | 0.050833 | 1.718 | 12.5934 | 0.00015512 | 4.587 | 39.615 | 9.2991e-05 | 24.603 | 2*380/50 ACSR | 41.7 | [6 empty] | 110 | 115 | 0 | 0 | B_BEN4_NKRA_2 | WADINKRA | BENBAN_4 |  |  |  |  | 0.0035497 | 0.026019 | 0.07508 | 0.0094773 | 0.081849 | 0.045008 | 0.050833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 1 | سلوا | BENBAN-1 | SELWA | مصر العليا | Circuit | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 54 | 2500/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.0039709 | 0.038071 | 0.088115 | 0.029161 | 0.11463 | 0.061318 | 0.025519 | 1.9219 | 18.4265 | 0.00018206 | 14.1138 | 55.4794 | 0.00012669 | 12.351 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 54 | [6 empty] | 109 | 112 | 0 | 0 | B_BEN1_SLWE_1 | BENBAN_1 | SELWAWST |  | محول تيارعند سلوا وفي محطة سلوا وصلت محولات تيار 1/2500 لكن لم يتم تركيبها بعد 2 ابريل 2023 |  |  | 0.0039709 | 0.038071 | 0.088115 | 0.029161 | 0.11463 | 0.061318 | 0.025519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بنبان 1 | سلوا | BENBAN-1 | SELWA | مصر العليا | Circuit | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 54 | 2500/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.0039709 | 0.038071 | 0.088115 | 0.029161 | 0.11463 | 0.061318 | 0.025519 | 1.9219 | 18.4265 | 0.00018206 | 14.1138 | 55.4794 | 0.00012669 | 12.351 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 54 | [6 empty] | 109 | 112 | 0 | 0 | B_BEN1_SLWE_2 | BENBAN_1 | SELWAWST |  | محول تيارعند سلوا وفي محطة سلوا وصلت محولات تيار 1/2500 لكن لم يتم تركيبها بعد 2 ابريل 2024 |  |  | 0.0039709 | 0.038071 | 0.088115 | 0.029161 | 0.11463 | 0.061318 | 0.025519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سلوا | اسنا الجديدة | SELWA | ISNA-NEW | مصر العليا | Circuit | 1 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 91 | 1600/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.0066918 | 0.064157 | 0.14849 | 0.049141 | 0.19317 | 0.10333 | 0.043003 | 3.2388 | 31.052 | 0.0003068 | 23.7844 | 93.4931 | 0.0002135 | 20.8137 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 91 | [6 empty] | 112 | 114 | 0 | 0 | B_NESNA_SELW_1 | SELWAWST | N_ESNA |  | 60كيلو ادفو + 31 كيلو الاقصر |  |  | 0.0066918 | 0.064157 | 0.14849 | 0.049141 | 0.19317 | 0.10333 | 0.043003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سلوا | اسنا الجديدة | SELWA | ISNA-NEW | مصر العليا | Circuit | 2 | 220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 91 | 1600/1 | 1600/1 | 1600 | 609.664 | 2500 | 0.0066918 | 0.064157 | 0.14849 | 0.049141 | 0.19317 | 0.10333 | 0.043003 | 3.2388 | 31.052 | 0.0003068 | 23.7844 | 93.4931 | 0.0002135 | 20.8137 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 91 | [6 empty] | 112 | 114 | 0 | 0 | B_NESNA_SELW_2 | SELWAWST | N_ESNA |  | 60كيلو ادفو + 31 كيلو الاقصر |  |  | 0.0066918 | 0.064157 | 0.14849 | 0.049141 | 0.19317 | 0.10333 | 0.043003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا الجديدة | الاقصر | ISNA-NEW | LXR-SHRQ | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 114 | 116 | 0 | 0 | B_LUXR_NESNA_1 | N_ESNA | LUXOR |  |  |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا الجديدة | الاقصر | ISNA-NEW | LXR-SHRQ | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 114 | 116 | 0 | 0 | B_LUXR_NESNA_2 | N_ESNA | LUXOR |  |  |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقصر | جنوب قنا | LXR-SHRQ | SOTH-QUENA | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 116 | 118 | 0 | 0 | B_LUXR_QENA_1 | LUXOR | QENA |  |  |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقصر | جنوب قنا | LXR-SHRQ | SOTH-QUENA | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 45 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 1.854 | 13.59 | 0.0001674 | 4.95 | 42.75 | 0.00010035 | 26.55 | 2*380/50 ACSR | 45 | [6 empty] | 116 | 118 | 0 | 0 | B_LUXR_QENA_2 | LUXOR | QENA |  |  |  |  | 0.0038306 | 0.028079 | 0.081022 | 0.010227 | 0.088326 | 0.048569 | 0.054855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 1 | توشكى 2 | TOSHKA-1 | TOSHKA-2 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 50 | 800/1 | 800/1 | 800 | 304.832 | 1500 | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 2.06 | 15.1 | 0.000186 | 5.5 | 47.5 | 0.0001115 | 29.5 | 2*380/50 ACSR | 50 | [6 empty] | 100 | 102 | 0 | 0 | B_TSH1_TSH2_1 | TOSHKA_1 | TOSHKA_2 |  | محول تيارلكل الدوائر ب توشكى 2 هي 800 امبير تم التاكد من المحطة في 1 ديسمبر 2020 |  |  | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 1 | توشكى 2 | TOSHKA-1 | TOSHKA-2 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 50 | 800/1 | 800/1 | 800 | 304.832 | 1500 | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 2.06 | 15.1 | 0.000186 | 5.5 | 47.5 | 0.0001115 | 29.5 | 2*380/50 ACSR | 50 | [6 empty] | 100 | 102 | 0 | 0 | B_TSH1_TSH2_2 | TOSHKA_1 | TOSHKA_2 |  | محول تيارلكل الدوائر ب توشكى 2 هي 800 امبير تم التاكد من المحطة في 1 ديسمبر 2020 |  |  | 0.0042562 | 0.031198 | 0.090024 | 0.011364 | 0.09814 | 0.053966 | 0.06095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طما | شرق سوهاج | TEMA | EST.SOHAG | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 76 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0064694 | 0.047421 | 0.13684 | 0.017273 | 0.14917 | 0.082028 | 0.092645 | 3.1312 | 22.952 | 0.00028272 | 8.36 | 72.2 | 0.00016948 | 44.84 | 2*380/50 ACSR | 76 | [6 empty] | 130 | 131 | 0 | 0 | B_SOHAG_TEMA_1 | TEMA | SOHG_EST |  |  |  |  | 0.0064694 | 0.047421 | 0.13684 | 0.017273 | 0.14917 | 0.082028 | 0.092645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
طما | شرق سوهاج | TEMA | EST.SOHAG | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 76 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0064694 | 0.047421 | 0.13684 | 0.017273 | 0.14917 | 0.082028 | 0.092645 | 3.1312 | 22.952 | 0.00028272 | 8.36 | 72.2 | 0.00016948 | 44.84 | 2*380/50 ACSR | 76 | [6 empty] | 130 | 131 | 0 | 0 | B_SOHAG_TEMA_2 | TEMA | SOHG_EST |  |  |  |  | 0.0064694 | 0.047421 | 0.13684 | 0.017273 | 0.14917 | 0.082028 | 0.092645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جرجا | شرق سوهاج | GERGA | EST.SOHAG | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 36 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 1.4832 | 10.872 | 0.00013392 | 3.96 | 34.2 | 8.028e-05 | 21.24 | 2*380/50 ACSR | 36 | [6 empty] | 128 | 131 | 0 | 0 | B_GRGA_SOHAG_1 | GERGA | SOHG_EST |  |  |  |  | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جرجا | شرق سوهاج | GERGA | EST.SOHAG | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 36 | 1600/1 | 2500/1 | 1200 | 457.248 | 1500 | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 1.4832 | 10.872 | 0.00013392 | 3.96 | 34.2 | 8.028e-05 | 21.24 | 2*380/50 ACSR | 36 | [6 empty] | 128 | 131 | 0 | 0 | B_GRGA_SOHAG_2 | GERGA | SOHG_EST |  |  |  |  | 0.0030645 | 0.022463 | 0.064817 | 0.0081818 | 0.070661 | 0.038856 | 0.043884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | توليد نجع حمادي | NAG-HAM | NAG.HAM-GEN | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 30.5 | 250/1 | 250/1 | 250 | 95.26 | 1500 | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 1.2566 | 9.211 | 0.00011346 | 3.355 | 28.975 | 6.8015e-05 | 17.995 | 2*380/50 ACSR | 30.5 | [6 empty] | 120 | 126 | 0 | 0 | B_NHYDR_NH50_1 | NHMDI500 | NHMDI_HY |  | محول تيار |  |  | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | توليد نجع حمادي | NAG-HAM | NAG.HAM-GEN | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 30.5 | 250/1 | 250/1 | 250 | 95.26 | 1500 | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 1.2566 | 9.211 | 0.00011346 | 3.355 | 28.975 | 6.8015e-05 | 17.995 | 2*380/50 ACSR | 30.5 | [6 empty] | 120 | 126 | 0 | 0 | B_NHYDR_NH50_2 | NHMDI500 | NHMDI_HY |  | محول تيار |  |  | 0.0025963 | 0.019031 | 0.054915 | 0.0069318 | 0.059866 | 0.032919 | 0.03718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 2.8 | 400/1 | 400/1 | 400 | 152.416 | 1500 | 0.00023835 | 0.0017471 | 0.0050413 | 0.00063636 | 0.0054959 | 0.0030221 | 0.0034132 | 0.11536 | 0.8456 | 1.0416e-05 | 0.308 | 2.66 | 6.244e-06 | 1.652 | 2*380/50 ACSR | 2.8 | [6 empty] | 120 | 122 | 0 | 0 | B_ALMN_NH50_1 | NHMDI500 | ALAMUNUM |  | ( CT at ALUMINUM AND NAG-HAM measure 400 and protection 800 ) محول تيارالقياس للالمنيوم ونجع حمادي 1/400/800 وتم اختيار 400 |  |  | 0.00023835 | 0.0017471 | 0.0050413 | 0.00063636 | 0.0054959 | 0.0030221 | 0.0034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 2.8 | 400/1 | 400/1 | 400 | 152.416 | 1500 | 0.00023835 | 0.0017471 | 0.0050413 | 0.00063636 | 0.0054959 | 0.0030221 | 0.0034132 | 0.11536 | 0.8456 | 1.0416e-05 | 0.308 | 2.66 | 6.244e-06 | 1.652 | 2*380/50 ACSR | 2.8 | [6 empty] | 120 | 122 | 0 | 0 | B_ALMN_NH50_2 | NHMDI500 | ALAMUNUM |  | ( CT at ALUMINUM AND NAG-HAM measure 400 and protection 800 ) محول تيارالقياس للالمنيوم ونجع حمادي 1/400/800 وتم اختيار 400 |  |  | 0.00023835 | 0.0017471 | 0.0050413 | 0.00063636 | 0.0054959 | 0.0030221 | 0.0034132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السد العالي | ربط الخزان | HIGH.DAM | ASWAN-DAM | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 12.5 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.001064 | 0.0077996 | 0.022506 | 0.0028409 | 0.024535 | 0.013492 | 0.015238 | 0.515 | 3.775 | 4.65e-05 | 1.375 | 11.875 | 2.7875e-05 | 7.375 | 2*380/50 ACSR | 12.5 | [6 empty] | 106 | 108 | 0 | 0 | B_ASW1_HDAM_1 | HIGHDAM | ASWNDAM1 |  | افاد م مصطفى مدير عام خطوط اسوان ان الخط ليس حراري وهو 2*380 ويتحمل 1200 امبير |  |  | 0.001064 | 0.0077996 | 0.022506 | 0.0028409 | 0.024535 | 0.013492 | 0.015238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
السد العالي | ربط الخزان | HIGH.DAM | ASWAN-DAM | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 12.5 | 1600/1 | 1600/1 | 1200 | 457.248 | 1500 | 0.001064 | 0.0077996 | 0.022506 | 0.0028409 | 0.024535 | 0.013492 | 0.015238 | 0.515 | 3.775 | 4.65e-05 | 1.375 | 11.875 | 2.7875e-05 | 7.375 | 2*380/50 ACSR | 12.5 | [6 empty] | 106 | 108 | 0 | 0 | B_ASW1_HDAM_2 | HIGHDAM | ASWNDAM1 |  | افاد م مصطفى مدير عام خطوط اسوان ان الخط ليس حراري وهو 2*380 ويتحمل 1200 امبير |  |  | 0.001064 | 0.0077996 | 0.022506 | 0.0028409 | 0.024535 | 0.013492 | 0.015238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ميديكوم | السد العالي | MEDECOM | HIGH.DAM | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 106 | 800/1 | 1600/1 | 800 | 304.832 | 1500 | 0.0090231 | 0.06614 | 0.19085 | 0.024091 | 0.20806 | 0.11441 | 0.12921 | 4.3672 | 32.012 | 0.00039432 | 11.66 | 100.7 | 0.00023638 | 62.54 | 2*380/50 ACSR | 106 | [6 empty] | 104 | 106 | 0 | 0 | B_HDAM_MEDI | MEDICOM | HIGHDAM |  | تم مراجعة المحطة وتبين انه مازال محولات التيار بميديكوم 800 امبير 1 ديسمبر 2020 CT at MEDCO 1/800/1600 and 800 is selected |  |  | 0.0090231 | 0.06614 | 0.19085 | 0.024091 | 0.20806 | 0.11441 | 0.12921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | توشكى 3 | TOSHKA-2 | TOSHKA-3 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 69 | 800/1 | 1250/1 | 800 | 304.832 | 1200 | 0.0058736 | 0.043054 | 0.12423 | 0.015682 | 0.13543 | 0.074473 | 0.084112 | 2.8428 | 20.838 | 0.00025668 | 7.59 | 65.55 | 0.00015387 | 40.71 | 2*380/50 ACSR | 69 | [6 empty] | 102 | 105 | 0 | 0 | B_TSH3_TSH2_1 | TOSHKA_2 | TOSHKA_3 |  | محول تيارلكل الدوائر ب توشكى 2 هي 800 امبير تم التاكد من المحطة في 1 ديسمبر 2020 |  |  | 0.0058736 | 0.043054 | 0.12423 | 0.015682 | 0.13543 | 0.074473 | 0.084112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | توشكى 3 | TOSHKA-2 | TOSHKA-3 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 69 | 800/1 | 1250/1 | 800 | 304.832 | 1200 | 0.0058736 | 0.043054 | 0.12423 | 0.015682 | 0.13543 | 0.074473 | 0.084112 | 2.8428 | 20.838 | 0.00025668 | 7.59 | 65.55 | 0.00015387 | 40.71 | 2*380/50 ACSR | 69 | [6 empty] | 102 | 105 | 0 | 0 | B_TSH3_TSH2_2 | TOSHKA_2 | TOSHKA_3 |  | محول تيارلكل الدوائر ب توشكى 2 هي 800 امبير تم التاكد من المحطة في 1 ديسمبر 2020 |  |  | 0.0058736 | 0.043054 | 0.12423 | 0.015682 | 0.13543 | 0.074473 | 0.084112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ميديكوم | توشكى 3 | MEDECOM | TOSHKA-3 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 85 | 800/1 | 1250/1 | 800 | 304.832 | 1200 | 0.0072355 | 0.053037 | 0.15304 | 0.019318 | 0.16684 | 0.091742 | 0.10362 | 3.502 | 25.67 | 0.0003162 | 9.35 | 80.75 | 0.00018955 | 50.15 | 2*380/50 ACSR | 85 | [6 empty] | 104 | 105 | 0 | -0.25 | B_MEDI_TSH3 | MEDICOM | TOSHKA_3 |  | تم مراجعة المحطة وتبين انه مازال محولات التيار بميديكوم 800 امبير 1 ديسمبر 2020 CT at MEDCO 1/800/1600 and 800 is selected |  |  | 0.0072355 | 0.053037 | 0.15304 | 0.019318 | 0.16684 | 0.091742 | 0.10362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 3 | السد العالي | TOSHKA-3 | HIGH.DAM | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 191 | 1250/1 | 1600/1 | 1200 | 457.248 | 1200 | 0.016259 | 0.11918 | 0.34389 | 0.043409 | 0.3749 | 0.20615 | 0.23283 | 7.8692 | 57.682 | 0.00071052 | 21.01 | 181.45 | 0.00042593 | 112.69 | 2*380/50 ACSR | 191 | [6 empty] | 105 | 106 | -0.25 | 0 | B_HDAM_TSH3 | TOSHKA_3 | HIGHDAM |  |  |  |  | 0.016259 | 0.11918 | 0.34389 | 0.043409 | 0.3749 | 0.20615 | 0.23283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | توشكى 4 | TOSHKA-2 | TOSHKA-4 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 70 | 800/1 | 1250/1 | 800 | 304.832 | 1200 | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 2.884 | 21.14 | 0.0002604 | 7.7 | 66.5 | 0.0001561 | 41.3 | 2*380/50 ACSR | 70 | [6 empty] | 102 | 133 | 0 | 0 | B_TSH4_TSH2_1 | TOSHKA_2 | TOSHKA_4 |  |  |  |  | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | توشكى 4 | TOSHKA-2 | TOSHKA-4 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 70 | 800/1 | 1250/1 | 800 | 304.832 | 1200 | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 2.884 | 21.14 | 0.0002604 | 7.7 | 66.5 | 0.0001561 | 41.3 | 2*380/50 ACSR | 70 | [6 empty] | 102 | 133 | 0 | 0 | B_TSH4_TSH2_2 | TOSHKA_2 | TOSHKA_4 |  |  |  |  | 0.0059587 | 0.043678 | 0.12603 | 0.015909 | 0.1374 | 0.075552 | 0.085331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | توشكى 4 | EST-OYNAT | TOSHKA-4 | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR | 320 | 1200/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.02724 | 0.19967 | 0.57615 | 0.072727 | 0.6281 | 0.34538 | 0.39008 | 13.184 | 96.64 | 0.0011904 | 35.2 | 304 | 0.0007136 | 188.8 | 2*380/50 ACSR | 320 | [6 empty] | 101 | 133 | -0.25 | 0 | B_AWNT_TSH4_1 | AWINAT | TOSHKA_4 |  |  |  |  | 0.02724 | 0.19967 | 0.57615 | 0.072727 | 0.6281 | 0.34538 | 0.39008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
شرق العوينات | توشكى 4 | EST-OYNAT | TOSHKA-4 | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR | 320 | 1200/1 | 1250/1 | 1200 | 457.248 | 1200 | 0.02724 | 0.19967 | 0.57615 | 0.072727 | 0.6281 | 0.34538 | 0.39008 | 13.184 | 96.64 | 0.0011904 | 35.2 | 304 | 0.0007136 | 188.8 | 2*380/50 ACSR | 320 | [6 empty] | 101 | 133 | -0.25 | 0 | B_AWNT_TSH4_2 | AWINAT | TOSHKA_4 |  |  |  |  | 0.02724 | 0.19967 | 0.57615 | 0.072727 | 0.6281 | 0.34538 | 0.39008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الهرم | ابوغالب | HARAM | ABO.GHALEB | القاهرة | Circuit & Cable | 1 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1200mm2 Thermal Invar 1*255/88 | 67.88 | 1600/1 | 1600/1 | 950 | 361.988 | 950 | 0.0084593 | 0.046601 | 0.21029 | 0.024831 | 0.13346 | 0.15602 | 0.084791 | 4.0943 | 22.5547 | 0.00043448 | 12.0184 | 64.5956 | 0.00032235 | 41.0388 | 2*405 AAAC | 19.14 | 2*380/50 ACSR | 28.38 | XLPE 1200mm2 | 3.6 | Thermal Invar 1*255/88 | 16.76 | 418 | 627 | 0 | 0 | B_GHALB_NHRM | N_HARAM | ABUGHALB |  | الجزء الحراري وجزء من الموصل 2*50/380 بطول 9.24 كم تابع لخطوط غرب البحيرة |  |  | 0.0019733 | 0.012101 | 0.030107 | 0.0051409 | 0.032823 | 0.020658 | 0.023332 | 0.0024158 | 0.017708 | 0.051098 | 0.00645 | 0.055705 | 0.030631 | 0.034595 | 0.00011678 | 0.0014846 | 0.10803 | 0.0015025 | 0.00052066 | 0.090605 | 0 | 0.0039534 | 0.015307 | 0.021053 | 0.011738 | 0.044414 | 0.014125 | 0.026864
الجيزة | ابوغالب | GIZA | ABO.GHALEB | القاهرة | Circuit & Cable | 1 | 220 | 2*405 AAAC 2*380/50 ACSR XLPE 1200mm2 Thermal Invar 1*255/88 | 71.28 | 1600/1 | 1600/1 | 950 | 361.988 | 950 | 0.0085696 | 0.048003 | 0.31231 | 0.02625 | 0.13395 | 0.24159 | 0.084791 | 4.1477 | 23.2334 | 0.00064528 | 12.7052 | 64.8336 | 0.00049915 | 41.0388 | 2*405 AAAC | 19.14 | 2*380/50 ACSR | 28.38 | XLPE 1200mm2 | 7 | Thermal Invar 1*255/88 | 16.76 | 416 | 627 | 0 | 0 | B_GIZA_GHALB | GIZA220 | ABUGHALB |  | الجزء الحراري وجزء من الموصل 2*50/380 بطول 9.24 كم تابع لخطوط غرب البحيرة |  |  | 0.0019733 | 0.012101 | 0.030107 | 0.0051409 | 0.032823 | 0.020658 | 0.023332 | 0.0024158 | 0.017708 | 0.051098 | 0.00645 | 0.055705 | 0.030631 | 0.034595 | 0.00022707 | 0.0028868 | 0.21006 | 0.0029215 | 0.0010124 | 0.17618 | 0 | 0.0039534 | 0.015307 | 0.021053 | 0.011738 | 0.044414 | 0.014125 | 0.026864
غرب اسيوط | بترول اسيوط | WST.ASSYUT | PETRL-ASSUT | مصر الوسطي | Cable | 1 | 220 | XLPE 2000mm2 Elswedy | 3.2 | 2000/1 | 2000/1 | 1600 | 609.664 | 1600 | 8.5091e-05 | 0.0011131 | 0.11093 | 0.0010165 | 0.00069408 | 0.092928 | 0 | 0.041184 | 0.53872 | 0.00022918 | 0.49197 | 0.33594 | 0.000192 | 0 | XLPE 2000mm2 Elswedy | 3.2 | [6 empty] | 201 | 203 | 0 | 0 | B_WASS_ASTKR_1 | N_ASSUTG | ASSUT_TK |  |  |  |  | 8.5091e-05 | 0.0011131 | 0.11093 | 0.0010165 | 0.00069408 | 0.092928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
غرب اسيوط | بترول اسيوط | WST.ASSYUT | PETRL-ASSUT | مصر الوسطي | Cable | 2 | 220 | XLPE 2000mm2 Elswedy | 3.2 | 2000/1 | 2000/1 | 1600 | 609.664 | 1600 | 8.5091e-05 | 0.0011131 | 0.11093 | 0.0010165 | 0.00069408 | 0.092928 | 0 | 0.041184 | 0.53872 | 0.00022918 | 0.49197 | 0.33594 | 0.000192 | 0 | XLPE 2000mm2 Elswedy | 3.2 | [6 empty] | 201 | 203 | 0 | 0 | B_WASS_ASTKR_2 | N_ASSUTG | ASSUT_TK |  |  |  |  | 8.5091e-05 | 0.0011131 | 0.11093 | 0.0010165 | 0.00069408 | 0.092928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي الصناعية | ابوطرطور | Industrial_NAG-HAM | A.TARTOR | مصر العليا | Circuit | 1 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 290 | 1250/1 | 600/1 | 600 | 228.624 | 750 | 0.048633 | 0.23643 | 0.40676 | 0.17347 | 0.56921 | 0.313 | 0.35351 | 23.5382 | 114.432 | 0.00084042 | 83.96 | 275.5 | 0.0006467 | 171.1 | 1*380/88 ACSR | 274 | 2*380/50 ACSR | 16 | [5 empty] | 224 | 0 | 0 |  |  | ABUTRTOR |  | يوجد 145 كم تابع لمصر الوسطى و 145 تابع لمصر العليا ومجموع طول الخط 290 كم |  |  | 0.047271 | 0.22645 | 0.37796 | 0.16983 | 0.53781 | 0.29573 | 0.33401 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي الصناعية | ابوطرطور | Industrial_NAG-HAM | A.TARTOR | مصر العليا | Circuit | 2 | 220 | 1*380/88 ACSR 2*380/50 ACSR | 290 | 1250/1 | 600/1 | 600 | 228.624 | 750 | 0.048633 | 0.23643 | 0.40676 | 0.17347 | 0.56921 | 0.313 | 0.35351 | 23.5382 | 114.432 | 0.00084042 | 83.96 | 275.5 | 0.0006467 | 171.1 | 1*380/88 ACSR | 274 | 2*380/50 ACSR | 16 | [5 empty] | 224 | 0 | 0 |  |  | ABUTRTOR |  | يوجد 145 كم تابع لمصر الوسطى و 145 تابع لمصر العليا ومجموع طول الخط 290 كم |  |  | 0.047271 | 0.22645 | 0.37796 | 0.16983 | 0.53781 | 0.29573 | 0.33401 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | سفاجا | SOTH-QUENA | SAFAGA | القناة | Circuit | 1 | 220 | 2*380/50 ACSR | 173 | 1600/1 | 1200/1 | 1200 | 457.248 | 1500 | 0.014726 | 0.10795 | 0.31148 | 0.039318 | 0.33957 | 0.18672 | 0.21089 | 7.1276 | 52.246 | 0.00064356 | 19.03 | 164.35 | 0.00038579 | 102.07 | 2*380/50 ACSR | 173 | [6 empty] | 118 | 398 | 0 | 0 | B_QENA_SFGA_1 | QENA | SAFAGA |  | طول 10 كم يتبع خطوط القناة و 163 كم يتبع خطوط شبكات قنا |  |  | 0.014726 | 0.10795 | 0.31148 | 0.039318 | 0.33957 | 0.18672 | 0.21089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | سفاجا | SOTH-QUENA | SAFAGA | القناة | Circuit | 2 | 220 | 2*380/50 ACSR | 173 | 1600/1 | 1200/1 | 1200 | 457.248 | 1500 | 0.014726 | 0.10795 | 0.31148 | 0.039318 | 0.33957 | 0.18672 | 0.21089 | 7.1276 | 52.246 | 0.00064356 | 19.03 | 164.35 | 0.00038579 | 102.07 | 2*380/50 ACSR | 173 | [6 empty] | 118 | 398 | 0 | 0 | B_QENA_SFGA_2 | QENA | SAFAGA |  | طول 10 كم يتبع خطوط القناة و 163 كم يتبع خطوط شبكات قنا |  |  | 0.014726 | 0.10795 | 0.31148 | 0.039318 | 0.33957 | 0.18672 | 0.21089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات 1 | زهراء المعادي | KURAIMAT-I | ZHRA.MAADI | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 87 | 1500/1 | 2000/1 | 1340 | 510.5936 | 1340 | 0.0074058 | 0.054285 | 0.15664 | 0.019773 | 0.17076 | 0.093901 | 0.10605 | 3.5844 | 26.274 | 0.00032364 | 9.57 | 82.65 | 0.00019401 | 51.33 | 2*380/50 ACSR | 87 | [6 empty] | 220 | 439 | 0 | 0 | B_ZHRAA_KOR_1 | KORIMAT | ZAHRAA_M |  |  |  |  | 0.0074058 | 0.054285 | 0.15664 | 0.019773 | 0.17076 | 0.093901 | 0.10605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات 1 | زهراء المعادي | KURAIMAT-I | ZHRA.MAADI | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 87 | 1500/1 | 2000/1 | 1340 | 510.5936 | 1340 | 0.0074058 | 0.054285 | 0.15664 | 0.019773 | 0.17076 | 0.093901 | 0.10605 | 3.5844 | 26.274 | 0.00032364 | 9.57 | 82.65 | 0.00019401 | 51.33 | 2*380/50 ACSR | 87 | [6 empty] | 220 | 439 | 0 | 0 | B_ZHRAA_KOR_2 | KORIMAT | ZAHRAA_M |  |  |  |  | 0.0074058 | 0.054285 | 0.15664 | 0.019773 | 0.17076 | 0.093901 | 0.10605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النرجس | زهراء المعادي | NARGES | ZHRA.MAADI | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1600mm2 Energya | 21.54 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1340 | 0.0015663 | 0.012128 | 0.19375 | 0.0056348 | 0.033505 | 0.15849 | 0.020114 | 0.75807 | 5.87 | 0.00040032 | 2.7272 | 16.2163 | 0.00032745 | 9.735 | 2*380/50 ACSR | 16.5 | XLPE 1600mm2 Energya | 5.04 |  |  |  |  | 413 | 439 | 0 | 0 | B_ZHRA_NARGS_1 | ALNARGES | ZAHRAA_M |  |  |  |  | 0.0014045 | 0.010295 | 0.029708 | 0.00375 | 0.032386 | 0.017809 | 0.020114 | 0.00016172 | 0.0018327 | 0.16405 | 0.0018848 | 0.0011184 | 0.14068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النرجس | زهراء المعادي | NARGES | ZHRA.MAADI | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1600mm2 Energya | 21.54 | 1600/1 | 2000/1 | 1080 | 411.5232 | 1340 | 0.0015663 | 0.012128 | 0.19375 | 0.0056348 | 0.033505 | 0.15849 | 0.020114 | 0.75807 | 5.87 | 0.00040032 | 2.7272 | 16.2163 | 0.00032745 | 9.735 | 2*380/50 ACSR | 16.5 | XLPE 1600mm2 Energya | 5.04 |  |  |  |  | 413 | 439 | 0 | 0 | B_ZHRA_NARGS_2 | ALNARGES | ZAHRAA_M |  |  |  |  | 0.0014045 | 0.010295 | 0.029708 | 0.00375 | 0.032386 | 0.017809 | 0.020114 | 0.00016172 | 0.0018327 | 0.16405 | 0.0018848 | 0.0011184 | 0.14068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النرجس | البساتين | NARGES | BASATEEN | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy XLPE 1600mm2 Energya | 24.956 | 1600/1 | 1200/1 | 1080 | 411.5232 | 1340 | 0.0016522 | 0.012995 | 0.2674 | 0.0070804 | 0.034015 | 0.24629 | 0.020114 | 0.79968 | 6.2894 | 0.00055248 | 3.4269 | 16.4631 | 0.00050887 | 9.735 | 2*380/50 ACSR | 16.5 | XLPE 1600mm2 Elswedy | 3.336 | XLPE 1600mm2 Energya | 5.12 |  |  | 413 | 424 | 0 | 0 | B_BSTN_NARGS_1 | ALNARGES | BASATEEN |  |  |  |  | 0.0014045 | 0.010295 | 0.029708 | 0.00375 | 0.032386 | 0.017809 | 0.020114 | 8.34e-05 | 0.00083745 | 0.071043 | 0.0014157 | 0.00049213 | 0.085575 | 0 | 0.00016428 | 0.0018618 | 0.16665 | 0.0019147 | 0.0011361 | 0.14291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
النرجس | البساتين | NARGES | BASATEEN | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1600mm2 Elswedy XLPE 1600mm2 Energya | 24.956 | 1600/1 | 1200/1 | 1080 | 411.5232 | 1340 | 0.0016522 | 0.012995 | 0.2674 | 0.0070804 | 0.034015 | 0.24629 | 0.020114 | 0.79968 | 6.2894 | 0.00055248 | 3.4269 | 16.4631 | 0.00050887 | 9.735 | 2*380/50 ACSR | 16.5 | XLPE 1600mm2 Elswedy | 3.336 | XLPE 1600mm2 Energya | 5.12 |  |  | 413 | 424 | 0 | 0 | B_BSTN_NARGS_2 | ALNARGES | BASATEEN |  |  |  |  | 0.0014045 | 0.010295 | 0.029708 | 0.00375 | 0.032386 | 0.017809 | 0.020114 | 8.34e-05 | 0.00083745 | 0.071043 | 0.0014157 | 0.00049213 | 0.085575 | 0 | 0.00016428 | 0.0018618 | 0.16665 | 0.0019147 | 0.0011361 | 0.14291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات (2و3) | الشرق | KURAIMAT2&3 | CAIRO-EST | القاهرة | Circuit & Cable | 1 | 220 | 2*380/50 ACSR XLPE 1200mm2 | 111.5 | 1600/1 | 800/1 | 800 | 304.832 | 950 | 0.0089908 | 0.067562 | 0.46872 | 0.027147 | 0.20158 | 0.34919 | 0.12434 | 4.3515 | 32.7002 | 0.00096844 | 13.139 | 97.565 | 0.00072146 | 60.18 | 2*380/50 ACSR | 102 | XLPE 1200mm2 | 9.5 |  |  |  |  | 218 | 426 | 0 | 0 | B_CEST_KRM2_1 | KURIMAT2 | CAIROEST |  | الكابل تايع للقاهرة والهوائي يتبع مصر الوسطى و محول تيار تم الاتصال بمحطة الشرق يوم 1 ديسمبر 2020 والتاكد ان محول التيار من جهة الشرق 800 امبير |  |  | 0.0086826 | 0.063645 | 0.18365 | 0.023182 | 0.20021 | 0.11009 | 0.12434 | 0.00030816 | 0.0039178 | 0.28508 | 0.0039649 | 0.001374 | 0.2391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الكريمات (2و3) | الشرق | KURAIMAT2&3 | CAIRO-EST | القاهرة | Circuit & Cable | 2 | 220 | 2*380/50 ACSR XLPE 1200mm2 | 111.5 | 1600/1 | 800/1 | 800 | 304.832 | 950 | 0.0089908 | 0.067562 | 0.46872 | 0.027147 | 0.20158 | 0.34919 | 0.12434 | 4.3515 | 32.7002 | 0.00096844 | 13.139 | 97.565 | 0.00072146 | 60.18 | 2*380/50 ACSR | 102 | XLPE 1200mm2 | 9.5 |  |  |  |  | 218 | 426 | 0 | 0 | B_CEST_KRM2_2 | KURIMAT2 | CAIROEST |  |  |  |  | 0.0086826 | 0.063645 | 0.18365 | 0.023182 | 0.20021 | 0.11009 | 0.12434 | 0.00030816 | 0.0039178 | 0.28508 | 0.0039649 | 0.001374 | 0.2391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف شرق | بني سويف الصناعية | BINSWF-EAST | INDS.BANISW | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 9.5 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.00080868 | 0.0059277 | 0.017105 | 0.0021591 | 0.018647 | 0.010254 | 0.011581 | 0.3914 | 2.869 | 3.534e-05 | 1.045 | 9.025 | 2.1185e-05 | 5.605 | 2*380/50 ACSR | 9.5 | [6 empty] | 214 | 217 | 0 | 0 | B_INDB_BSUF_1 | BSUEFEST | IND_BNSF |  |  |  |  | 0.00080868 | 0.0059277 | 0.017105 | 0.0021591 | 0.018647 | 0.010254 | 0.011581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف شرق | بني سويف الصناعية | BINSWF-EAST | INDS.BANISW | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 9.5 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.00080868 | 0.0059277 | 0.017105 | 0.0021591 | 0.018647 | 0.010254 | 0.011581 | 0.3914 | 2.869 | 3.534e-05 | 1.045 | 9.025 | 2.1185e-05 | 5.605 | 2*380/50 ACSR | 9.5 | [6 empty] | 214 | 217 | 0 | 0 | B_INDB_BSUF_2 | BSUEFEST | IND_BNSF |  |  |  |  | 0.00080868 | 0.0059277 | 0.017105 | 0.0021591 | 0.018647 | 0.010254 | 0.011581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت العريش | بني سويف الصناعية | ARISH-CMNT | INDS.BANISW | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 6.5 | 2000/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.2678 | 1.963 | 2.418e-05 | 0.715 | 6.175 | 1.4495e-05 | 3.835 | 2*380/50 ACSR | 6.5 | [6 empty] | 213 | 217 | 0 | 0 | B_INDB_ARSH_1 | ARISH_CM | IND_BNSF |  |  |  |  | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت العريش | بني سويف الصناعية | ARISH-CMNT | INDS.BANISW | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 6.5 | 2000/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0.2678 | 1.963 | 2.418e-05 | 0.715 | 6.175 | 1.4495e-05 | 3.835 | 2*380/50 ACSR | 6.5 | [6 empty] | 213 | 217 | 0 | 0 | B_INDB_ARSH_2 | ARISH_CM | IND_BNSF |  |  |  |  | 0.00055331 | 0.0040558 | 0.011703 | 0.0014773 | 0.012758 | 0.0070156 | 0.0079236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حديد المصريين | بني سويف الصناعية | HADED-MSREN | INDS.BANISW | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR | 16 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0.6592 | 4.832 | 5.952e-05 | 1.76 | 15.2 | 3.568e-05 | 9.44 | 2*380/50 ACSR | 16 | [6 empty] | 215 | 217 | 0 | 0 | B_STEEL_INDS_1 | STEEL_EG | IND_BNSF |  |  |  |  | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حديد المصريين | بني سويف الصناعية | HADED-MSREN | INDS.BANISW | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR | 16 | 1600/1 | 2500/1 | 1340 | 510.5936 | 1340 | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0.6592 | 4.832 | 5.952e-05 | 1.76 | 15.2 | 3.568e-05 | 9.44 | 2*380/50 ACSR | 16 | [6 empty] | 215 | 217 | 0 | 0 | B_STEEL_INDS_2 | STEEL_EG | IND_BNSF |  |  |  |  | 0.001362 | 0.0099835 | 0.028808 | 0.0036364 | 0.031405 | 0.017269 | 0.019504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حديد المصريين | الزعفرانة 2 | HADED-MSREN | ZAFRANA-II | مصر الوسطي | Circuit | 1 | 220 | 2*380/50 ACSR 2*405 AAAC | 152 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.013676 | 0.095182 | 0.26435 | 0.03624 | 0.28818 | 0.16406 | 0.18529 | 6.6191 | 46.068 | 0.00054617 | 17.54 | 139.48 | 0.00033896 | 89.68 | 2*380/50 ACSR | 111 | 2*405 AAAC | 41 |  |  |  |  | 215 | 301 | 0 | 0 | B_STEEL_ZAF2_1 | STEEL_EG | ZAFRANA2 |  | الجزء الخاص بخطوط بني سويف بمنطقة مصر الوسطى طوله 72 كم وبه متنقلة بني عريضة والجزء الخاص بمنطة القناة طوله 80 كم |  |  | 0.0094488 | 0.06926 | 0.19985 | 0.025227 | 0.21787 | 0.1198 | 0.13531 | 0.0042271 | 0.025921 | 0.064493 | 0.011012 | 0.07031 | 0.044252 | 0.049979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
حديد المصريين | الزعفرانة 2 | HADED-MSREN | ZAFRANA-II | مصر الوسطي | Circuit | 2 | 220 | 2*380/50 ACSR 2*405 AAAC | 152 | 1600/1 | 1600/1 | 1340 | 510.5936 | 1340 | 0.013676 | 0.095182 | 0.26435 | 0.03624 | 0.28818 | 0.16406 | 0.18529 | 6.6191 | 46.068 | 0.00054617 | 17.54 | 139.48 | 0.00033896 | 89.68 | 2*380/50 ACSR | 111 | 2*405 AAAC | 41 |  |  |  |  | 215 | 301 | 0 | 0 | B_STEEL_ZAF2_2 | STEEL_EG | ZAFRANA2 |  | الجزء الخاص بخطوط بني سويف بمنطقة مصر الوسطى طوله 72 كم وبه متنقلة بني عريضة والجزء الخاص بمنطة القناة طوله 80 كم |  |  | 0.0094488 | 0.06926 | 0.19985 | 0.025227 | 0.21787 | 0.1198 | 0.13531 | 0.0042271 | 0.025921 | 0.064493 | 0.011012 | 0.07031 | 0.044252 | 0.049979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | وادي حلفا | TOSHKA-2 | WADI-HALFA | مصر العليا | Circuit | 1 | 220 | 2*380/50 ACSR 2*240/40 ACO | 169 | 2000/1 |  | 1000 | 381.04 | 1500 | 0.01948 | 0.1204 | 0.27218 | 0.055021 | 0.33171 | 0.18241 | 0.20601 | 9.4284 | 58.274 | 0.00056235 | 26.63 | 160.55 | 0.00037687 | 99.71 | 2*380/50 ACSR | 102 | 2*240/40 ACO | 67 |  |  |  |  | 102 | 99 | 0 | 0 | B_TSH2_HALFA_1 | TOSHKA_2 | W_HALFA |  | طول 102 كم يتبع الجانب المصري ونوع الموصل 2*380 و 67 كم يتبع الجانب السوداني ونوع الموصل 2*240/40 ACO |  |  | 0.0086826 | 0.063645 | 0.18365 | 0.023182 | 0.20021 | 0.11009 | 0.12434 | 0.010798 | 0.056756 | 0.088528 | 0.031839 | 0.13151 | 0.072314 | 0.081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
توشكى 2 | وادي حلفا | TOSHKA-2 | WADI-HALFA | مصر العليا | Circuit | 2 | 220 | 2*380/50 ACSR 2*240/40 ACO | 169 | 2000/1 |  | 1000 | 381.04 | 1500 | 0.01948 | 0.1204 | 0.27218 | 0.055021 | 0.33171 | 0.18241 | 0.20601 | 9.4284 | 58.274 | 0.00056235 | 26.63 | 160.55 | 0.00037687 | 99.71 | 2*380/50 ACSR | 102 | 2*240/40 ACO | 67 |  |  |  |  | 102 | 99 | 0 | 0 | B_TSH2_HALFA_2 | TOSHKA_2 | W_HALFA |  |  |  |  | 0.0086826 | 0.063645 | 0.18365 | 0.023182 | 0.20021 | 0.11009 | 0.12434 | 0.010798 | 0.056756 | 0.088528 | 0.031839 | 0.13151 | 0.072314 | 0.081674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الغرب | CAIRO.500 | CAIRO-WST | القاهرة | Circuit | 1 | 220 | 2*405 AAAC | 11 | 1500/1 | 1100/1 | 1200 | 457.248 | 1200 | 0.0011341 | 0.0069545 | 0.017303 | 0.0029545 | 0.018864 | 0.011873 | 0.013409 | 0.5489 | 3.366 | 3.575e-05 | 1.43 | 9.13 | 2.453e-05 | 6.49 | 2*405 AAAC | 11 | [6 empty] | 400 | 402 | 0 | 0 | B_C500_CWST_1 | CAIRO500 | CAIROWST |  | الدائرتين مفصولتين لحين توصيل هذه الدوائر مع الغرب /باسوس من خارج محطة الغرب بحيث تصبح القاهرة 500 متصلة مباشرة ب باسوس دون الدخول على الغرب |  |  | 0.0011341 | 0.0069545 | 0.017303 | 0.0029545 | 0.018864 | 0.011873 | 0.013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
القاهرة 500 | الغرب | CAIRO.500 | CAIRO-WST | القاهرة | Circuit | 2 | 220 | 2*405 AAAC | 11 | 1500/1 | 1100/1 | 1200 | 457.248 | 1200 | 0.0011341 | 0.0069545 | 0.017303 | 0.0029545 | 0.018864 | 0.011873 | 0.013409 | 0.5489 | 3.366 | 3.575e-05 | 1.43 | 9.13 | 2.453e-05 | 6.49 | 2*405 AAAC | 11 | [6 empty] | 400 | 402 | 0 | 0 | B_C500_CWST_2 | CAIRO500 | CAIROWST |  | الدائرتين مفصولتين لحين توصيل هذه الدوائر مع الغرب /باسوس من خارج محطة الغرب بحيث تصبح القاهرة 500 متصلة مباشرة ب باسوس دون الدخول على الغرب |  |  | 0.0011341 | 0.0069545 | 0.017303 | 0.0029545 | 0.018864 | 0.011873 | 0.013409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت أ | اسيوط 500 | ASMNT-A | ASSYUT | مصر العليا | Circuit | 1 | 132 | 1*240 AAAC | 3.5 | 600/1 | 1200/1 | 400 | 91.4496 | 400 | 0.0023904 | 0.0080349 | 0.001738 | 0.014664 | 0.025712 | 0.0010428 | 0.015266 | 0.4165 | 1.4 | 9.975e-06 | 2.555 | 4.48 | 5.985e-06 | 2.66 | 1*240 AAAC | 3.5 | [6 empty] | 922 | 923 | 0 | 0 | [7 empty] | 0.0023904 | 0.0080349 | 0.001738 | 0.014664 | 0.025712 | 0.0010428 | 0.015266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت أ | اسيوط 500 | ASMNT-A | ASSYUT | مصر العليا | Circuit | 2 | 132 | 1*240 AAAC | 3.5 | 600/1 | 1200/1 | 400 | 91.4496 | 400 | 0.0023904 | 0.0080349 | 0.001738 | 0.014664 | 0.025712 | 0.0010428 | 0.015266 | 0.4165 | 1.4 | 9.975e-06 | 2.555 | 4.48 | 5.985e-06 | 2.66 | 1*240 AAAC | 3.5 | [6 empty] | 922 | 923 | 0 | 0 | [7 empty] | 0.0023904 | 0.0080349 | 0.001738 | 0.014664 | 0.025712 | 0.0010428 | 0.015266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت ب | اسيوط 500 | ASMNT-B | ASSYUT | مصر العليا | Circuit | 1 | 132 | 1*380/50 ACSR | 5.6 | 600/1 | 1200/1 | 600 | 137.1744 | 670 | 0.0026837 | 0.012856 | 0.0027809 | 0.0096419 | 0.030533 | 0.0021759 | 0.018962 | 0.4676 | 2.24 | 1.596e-05 | 1.68 | 5.32 | 1.2488e-05 | 3.304 | 1*380/50 ACSR | 5.6 | [6 empty] | 921 | 923 | 0 | 0 | [7 empty] | 0.0026837 | 0.012856 | 0.0027809 | 0.0096419 | 0.030533 | 0.0021759 | 0.018962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت ب | اسيوط 500 | ASMNT-B | ASSYUT | مصر العليا | Circuit | 2 | 132 | 1*380/50 ACSR | 5.6 | 600/1 | 1200/1 | 600 | 137.1744 | 670 | 0.0026837 | 0.012856 | 0.0027809 | 0.0096419 | 0.030533 | 0.0021759 | 0.018962 | 0.4676 | 2.24 | 1.596e-05 | 1.68 | 5.32 | 1.2488e-05 | 3.304 | 1*380/50 ACSR | 5.6 | [6 empty] | 921 | 923 | 0 | 0 | [7 empty] | 0.0026837 | 0.012856 | 0.0027809 | 0.0096419 | 0.030533 | 0.0021759 | 0.018962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنيا | سمالوط | MENIA | SAMALUT | مصر العليا | Circuit | 1 | 132 | 1*240 AAAC | 39 | 600/1 | 750/1 | 300 | 68.5872 | 400 | 0.026636 | 0.089532 | 0.019367 | 0.1634 | 0.2865 | 0.01162 | 0.17011 | 4.641 | 15.6 | 0.00011115 | 28.47 | 49.92 | 6.669e-05 | 29.64 | 1*240 AAAC | 39 | [6 empty] | 925 | 926 | 0 | 0 | [7 empty] | 0.026636 | 0.089532 | 0.019367 | 0.1634 | 0.2865 | 0.01162 | 0.17011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
المنيا | سمالوط | MENIA | SAMALUT | مصر العليا | Circuit | 2 | 132 | 1*240 AAAC | 39 | 600/1 | 750/1 | 300 | 68.5872 | 400 | 0.026636 | 0.089532 | 0.019367 | 0.1634 | 0.2865 | 0.01162 | 0.17011 | 4.641 | 15.6 | 0.00011115 | 28.47 | 49.92 | 6.669e-05 | 29.64 | 1*240 AAAC | 39 | [6 empty] | 925 | 926 | 0 | 0 | [7 empty] | 0.026636 | 0.089532 | 0.019367 | 0.1634 | 0.2865 | 0.01162 | 0.17011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | اسمنت المنيا | SAMALUT | CMT-MENIA | مصر العليا | Circuit | 1 | 132 | 2*380/50 ACSR | 17 | 750/1 | 800/1 | 750 | 171.468 | 1200 | 0.0040197 | 0.029465 | 0.011019 | 0.010732 | 0.092688 | 0.0066054 | 0.057564 | 0.7004 | 5.134 | 6.324e-05 | 1.87 | 16.15 | 3.791e-05 | 10.03 | 2*380/50 ACSR | 17 | [6 empty] | 926 | 927 | 0 | 0 | [7 empty] | 0.0040197 | 0.029465 | 0.011019 | 0.010732 | 0.092688 | 0.0066054 | 0.057564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | اسمنت المنيا | SAMALUT | CMT-MENIA | مصر العليا | Circuit | 2 | 132 | 2*380/50 ACSR | 17 | 750/1 | 800/1 | 750 | 171.468 | 1200 | 0.0040197 | 0.029465 | 0.011019 | 0.010732 | 0.092688 | 0.0066054 | 0.057564 | 0.7004 | 5.134 | 6.324e-05 | 1.87 | 16.15 | 3.791e-05 | 10.03 | 2*380/50 ACSR | 17 | [6 empty] | 926 | 927 | 0 | 0 | [7 empty] | 0.0040197 | 0.029465 | 0.011019 | 0.010732 | 0.092688 | 0.0066054 | 0.057564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | مغاغة | SAMALUT | MAGAGA | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 49.6 | 750/1 | 300/1 | 300 | 68.5872 | 300 | 0.07686 | 0.11956 | 0.023507 | 0.20781 | 0.36437 | 0.014778 | 0.21635 | 13.392 | 20.832 | 0.00013491 | 36.208 | 63.488 | 8.4816e-05 | 37.696 | 1*120/21 ACSR | 49.6 | [6 empty] | 926 | 929 | 0 | 0 | [7 empty] | 0.07686 | 0.11956 | 0.023507 | 0.20781 | 0.36437 | 0.014778 | 0.21635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | مغاغة | SAMALUT | MAGAGA | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 49.6 | 750/1 | 300/1 | 300 | 68.5872 | 300 | 0.07686 | 0.11956 | 0.023507 | 0.20781 | 0.36437 | 0.014778 | 0.21635 | 13.392 | 20.832 | 0.00013491 | 36.208 | 63.488 | 8.4816e-05 | 37.696 | 1*120/21 ACSR | 49.6 | [6 empty] | 926 | 929 | 0 | 0 | [7 empty] | 0.07686 | 0.11956 | 0.023507 | 0.20781 | 0.36437 | 0.014778 | 0.21635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | الواحات البحرية | SAMALUT | WAHAT | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 202 | 750/1 | 300/1 | 300 | 68.5872 | 300 | 0.31302 | 0.48691 | 0.095734 | 0.8463 | 1.4839 | 0.060186 | 0.88108 | 54.54 | 84.84 | 0.00054944 | 147.46 | 258.56 | 0.00034542 | 153.52 | 1*120/21 ACSR | 202 | [6 empty] | 926 | 928 | 0 | 0 | [7 empty] | 0.31302 | 0.48691 | 0.095734 | 0.8463 | 1.4839 | 0.060186 | 0.88108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سمالوط | الواحات البحرية | SAMALUT | WAHAT | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 202 | 750/1 | 300/1 | 300 | 68.5872 | 300 | 0.31302 | 0.48691 | 0.095734 | 0.8463 | 1.4839 | 0.060186 | 0.88108 | 54.54 | 84.84 | 0.00054944 | 147.46 | 258.56 | 0.00034542 | 153.52 | 1*120/21 ACSR | 202 | [6 empty] | 926 | 928 | 0 | 0 | [7 empty] | 0.31302 | 0.48691 | 0.095734 | 0.8463 | 1.4839 | 0.060186 | 0.88108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف غرب | دمو | BNISWF.WEST | DEMO | مصر العليا | Circuit | 1 | 132 | 1*380/50 ACSR | 33 | 800/1 | 800/1 | 600 | 137.1744 | 670 | 0.015814 | 0.075758 | 0.016387 | 0.056818 | 0.17992 | 0.012822 | 0.11174 | 2.7555 | 13.2 | 9.405e-05 | 9.9 | 31.35 | 7.359e-05 | 19.47 | 1*380/50 ACSR | 33 | [6 empty] | 930 | 931 | 0 | 0 | [7 empty] | 0.015814 | 0.075758 | 0.016387 | 0.056818 | 0.17992 | 0.012822 | 0.11174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
بني سويف غرب | دمو | BNISWF.WEST | DEMO | مصر العليا | Circuit | 2 | 132 | 1*380/50 ACSR | 33 | 800/1 | 800/1 | 600 | 137.1744 | 670 | 0.015814 | 0.075758 | 0.016387 | 0.056818 | 0.17992 | 0.012822 | 0.11174 | 2.7555 | 13.2 | 9.405e-05 | 9.9 | 31.35 | 7.359e-05 | 19.47 | 1*380/50 ACSR | 33 | [6 empty] | 930 | 931 | 0 | 0 | [7 empty] | 0.015814 | 0.075758 | 0.016387 | 0.056818 | 0.17992 | 0.012822 | 0.11174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | المنيا | MALAWI | MENIA | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 40.6 | 600/1 | 600/1 | 300 | 68.5872 | 300 | 0.062913 | 0.097865 | 0.019242 | 0.1701 | 0.29826 | 0.012097 | 0.17709 | 10.962 | 17.052 | 0.00011043 | 29.638 | 51.968 | 6.9426e-05 | 30.856 | 1*120/21 ACSR | 40.6 | [6 empty] | 924 | 925 | 0 | 0 | [7 empty] | 0.062913 | 0.097865 | 0.019242 | 0.1701 | 0.29826 | 0.012097 | 0.17709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ملوي | المنيا | MALAWI | MENIA | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 40.6 | 600/1 | 600/1 | 300 | 68.5872 | 300 | 0.062913 | 0.097865 | 0.019242 | 0.1701 | 0.29826 | 0.012097 | 0.17709 | 10.962 | 17.052 | 0.00011043 | 29.638 | 51.968 | 6.9426e-05 | 30.856 | 1*120/21 ACSR | 40.6 | [6 empty] | 924 | 925 | 0 | 0 | [7 empty] | 0.062913 | 0.097865 | 0.019242 | 0.1701 | 0.29826 | 0.012097 | 0.17709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسمنت ب | اسمنت أ | ASMNT-B | ASMNT-A | مصر العليا | Circuit | 1 | 132 | 1*240 AAAC | 1.2 | 600/1 | 600/1 | 400 | 91.4496 | 400 | 0.00081956 | 0.0027548 | 0.0005959 | 0.0050275 | 0.0088154 | 0.00035754 | 0.0052342 | 0.1428 | 0.48 | 3.42e-06 | 0.876 | 1.536 | 2.052e-06 | 0.912 | 1*240 AAAC | 1.2 | [6 empty] | 921 | 922 | 0 | 0 | [7 empty] | 0.00081956 | 0.0027548 | 0.0005959 | 0.0050275 | 0.0088154 | 0.00035754 | 0.0052342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط البخارية | اسمنت أ | ASYOTGEN | ASMNT-A | مصر العليا | Circuit | 1 | 132 | 1*240 AAAC | 25 | 600/1 | 600/1 | 400 | 91.4496 | 400 | 0.017074 | 0.057392 | 0.012415 | 0.10474 | 0.18365 | 0.0074488 | 0.10904 | 2.975 | 10 | 7.125e-05 | 18.25 | 32 | 4.275e-05 | 19 | 1*240 AAAC | 25 | [6 empty] | 920 | 922 | 0 | 0 | [7 empty] | 0.017074 | 0.057392 | 0.012415 | 0.10474 | 0.18365 | 0.0074488 | 0.10904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط البخارية | اسمنت ب | ASYOTGEN | ASMNT-B | مصر العليا | Circuit | 1 | 132 | 1*240 AAAC | 25 | 600/1 | 600/1 | 300 | 68.5872 | 400 | 0.017074 | 0.057392 | 0.012415 | 0.10474 | 0.18365 | 0.0074488 | 0.10904 | 2.975 | 10 | 7.125e-05 | 18.25 | 32 | 4.275e-05 | 19 | 1*240 AAAC | 25 | [6 empty] | 920 | 921 | 0 | 0 | [7 empty] | 0.017074 | 0.057392 | 0.012415 | 0.10474 | 0.18365 | 0.0074488 | 0.10904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | ملوي | ASSYUT | MALAWI | مصر العليا | Circuit | 1 | 132 | 1*235.6 AAAC | 72 | 600/1 | 600/1 | 400 | 91.4496 | 400 | 0.049174 | 0.16529 | 0.035754 | 0.30165 | 0.52893 | 0.021452 | 0.31405 | 8.568 | 28.8 | 0.0002052 | 52.56 | 92.16 | 0.00012312 | 54.72 | 1*235.6 AAAC | 72 | [6 empty] | 923 | 924 | 0 | 0 | [7 empty] | 0.049174 | 0.16529 | 0.035754 | 0.30165 | 0.52893 | 0.021452 | 0.31405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسيوط 500 | ملوي | ASSYUT | MALAWI | مصر العليا | Circuit | 2 | 132 | 1*235.6 AAAC | 72 | 600/1 | 600/1 | 400 | 91.4496 | 400 | 0.049174 | 0.16529 | 0.035754 | 0.30165 | 0.52893 | 0.021452 | 0.31405 | 8.568 | 28.8 | 0.0002052 | 52.56 | 92.16 | 0.00012312 | 54.72 | 1*235.6 AAAC | 72 | [6 empty] | 923 | 924 | 0 | 0 | [7 empty] | 0.049174 | 0.16529 | 0.035754 | 0.30165 | 0.52893 | 0.021452 | 0.31405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مغاغة | بني سويف غرب | MAGAGA | BNISWF.WEST | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 59.7 | 300/1 | 400/1 | 300 | 68.5872 | 300 | 0.09251 | 0.1439 | 0.028294 | 0.25012 | 0.43857 | 0.017788 | 0.2604 | 16.119 | 25.074 | 0.00016238 | 43.581 | 76.416 | 0.00010209 | 45.372 | 1*120/21 ACSR | 59.7 | [6 empty] | 929 | 930 | 0 | 0 | [7 empty] | 0.09251 | 0.1439 | 0.028294 | 0.25012 | 0.43857 | 0.017788 | 0.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
مغاغة | بني سويف غرب | MAGAGA | BNISWF.WEST | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 59.7 | 300/1 | 400/1 | 300 | 68.5872 | 300 | 0.09251 | 0.1439 | 0.028294 | 0.25012 | 0.43857 | 0.017788 | 0.2604 | 16.119 | 25.074 | 0.00016238 | 43.581 | 76.416 | 0.00010209 | 45.372 | 1*120/21 ACSR | 59.7 | [6 empty] | 929 | 930 | 0 | 0 | [7 empty] | 0.09251 | 0.1439 | 0.028294 | 0.25012 | 0.43857 | 0.017788 | 0.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | كوم امبو | ASWAN-DAM | KOMOMBO | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 51.7 | 750/1 | 600/5 | 600 | 137.1744 | 650 | 0.029672 | 0.11513 | 0.025673 | 0.073289 | 0.29968 | 0.015404 | 0.1988 | 5.17 | 20.0596 | 0.00014735 | 12.7699 | 52.217 | 8.8407e-05 | 34.639 | 1*323/75 ACSR | 51.7 | [6 empty] | 901 | 903 | 0 | 0 | [7 empty] | 0.029672 | 0.11513 | 0.025673 | 0.073289 | 0.29968 | 0.015404 | 0.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | كوم امبو | ASWAN-DAM | KOMOMBO | مصر العليا | Circuit | 2 | 132 | 1*326/62.5 ACSR | 51 | 750/1 | 600/5 | 600 | 137.1744 | 650 | 0.02927 | 0.11357 | 0.025326 | 0.072297 | 0.29563 | 0.015195 | 0.19611 | 5.1 | 19.788 | 0.00014535 | 12.597 | 51.51 | 8.721e-05 | 34.17 | 1*326/62.5 ACSR | 51 | [6 empty] | 901 | 903 | 0 | 0 | [7 empty] | 0.02927 | 0.11357 | 0.025326 | 0.072297 | 0.29563 | 0.015195 | 0.19611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كيما | ربط الخزان | KEMA | ASWAN-DAM | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 11 | 600/5 | 750/1 | 600 | 137.1744 | 650 | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 1.1 | 4.268 | 3.135e-05 | 2.717 | 11.11 | 1.881e-05 | 7.37 | 1*323/75 ACSR | 11 | [6 empty] | 900 | 901 | 0 | 0 | [7 empty] | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كيما | ربط الخزان | KEMA | ASWAN-DAM | مصر العليا | Circuit | 2 | 132 | 1*323/75 ACSR | 11 | 600/5 | 750/1 | 600 | 137.1744 | 650 | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 1.1 | 4.268 | 3.135e-05 | 2.717 | 11.11 | 1.881e-05 | 7.37 | 1*323/75 ACSR | 11 | [6 empty] | 900 | 901 | 0 | 0 | [7 empty] | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كيما | ربط الخزان | KEMA | ASWAN-DAM | مصر العليا | Circuit | 3 | 132 | 1*323/75 ACSR | 11 | 600/5 | 750/1 | 600 | 137.1744 | 650 | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 1.1 | 4.268 | 3.135e-05 | 2.717 | 11.11 | 1.881e-05 | 7.37 | 1*323/75 ACSR | 11 | [6 empty] | 900 | 901 | 0 | 0 | [7 empty] | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كيما | ربط الخزان | KEMA | ASWAN-DAM | مصر العليا | Circuit | 4 | 132 | 1*323/75 ACSR | 11 | 600/5 | 750/1 | 600 | 137.1744 | 650 | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 1.1 | 4.268 | 3.135e-05 | 2.717 | 11.11 | 1.881e-05 | 7.37 | 1*323/75 ACSR | 11 | [6 empty] | 900 | 901 | 0 | 0 | [7 empty] | 0.0063131 | 0.024495 | 0.0054624 | 0.015593 | 0.063763 | 0.0032775 | 0.042298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | الفيروسيليكون | ASWAN-DAM | FEROSLKN | مصر العليا | Circuit | 1 | 132 | 1*326/62.5 ACSR | 121 | 750/1 | 800/1 | 650 | 148.6056 | 650 | 0.069444 | 0.26944 | 0.060087 | 0.17153 | 0.70139 | 0.036052 | 0.46528 | 12.1 | 46.948 | 0.00034485 | 29.887 | 122.21 | 0.00020691 | 81.07 | 1*326/62.5 ACSR | 121 | [6 empty] | 901 | 904 | 0 | 0 |  |  |  |  | 51كم اسوان+ 70كم ادفو |  |  | 0.069444 | 0.26944 | 0.060087 | 0.17153 | 0.70139 | 0.036052 | 0.46528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | ادفو | ASWAN-DAM | IDFO | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 109.7 | 600/5 | 600/5 | 600 | 137.1744 | 650 | 0.062959 | 0.24428 | 0.054475 | 0.15551 | 0.63589 | 0.032685 | 0.42183 | 10.97 | 42.5636 | 0.00031265 | 27.0959 | 110.797 | 0.00018759 | 73.499 | 1*323/75 ACSR | 109.7 | [6 empty] | 901 | 905 | 0 | 0 |  |  |  |  | 58كم ادفو + 51.7كم اسوان |  |  | 0.062959 | 0.24428 | 0.054475 | 0.15551 | 0.63589 | 0.032685 | 0.42183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا | الاقصر شرق | ISNA | LXR-SHRQ | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 96 | 600/5 | 800/1 | 400 | 91.4496 | 650 | 0.055096 | 0.21377 | 0.047672 | 0.13609 | 0.55647 | 0.028603 | 0.36915 | 9.6 | 37.248 | 0.0002736 | 23.712 | 96.96 | 0.00016416 | 64.32 | 1*323/75 ACSR | 96 | [6 empty] | 906 | 908 | 0 | 0 | [7 empty] | 0.055096 | 0.21377 | 0.047672 | 0.13609 | 0.55647 | 0.028603 | 0.36915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا | توليد اسنا | ISNA | ISNA-GEN | مصر العليا | Circuit | 1 | 132 | 1*380/50 ACSR | 2 | 1000/1 | 500/1 | 500 | 114.312 | 670 | 0.00095845 | 0.0045914 | 0.00099317 | 0.0034435 | 0.010904 | 0.00077711 | 0.0067723 | 0.167 | 0.8 | 5.7e-06 | 0.6 | 1.9 | 4.46e-06 | 1.18 | 1*380/50 ACSR | 2 | [6 empty] | 906 | 907 | 0 | 0 | [7 empty] | 0.00095845 | 0.0045914 | 0.00099317 | 0.0034435 | 0.010904 | 0.00077711 | 0.0067723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا | توليد اسنا | ISNA | ISNA-GEN | مصر العليا | Circuit | 2 | 132 | 1*380/50 ACSR | 2 | 1000/1 | 500/1 | 500 | 114.312 | 670 | 0.00095845 | 0.0045914 | 0.00099317 | 0.0034435 | 0.010904 | 0.00077711 | 0.0067723 | 0.167 | 0.8 | 5.7e-06 | 0.6 | 1.9 | 4.46e-06 | 1.18 | 1*380/50 ACSR | 2 | [6 empty] | 906 | 907 | 0 | 0 | [7 empty] | 0.00095845 | 0.0045914 | 0.00099317 | 0.0034435 | 0.010904 | 0.00077711 | 0.0067723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
اسنا | جنوب قنا | ISNA | SOTH-QUENA | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 145 | 600/5 | 500/1 | 500 | 114.312 | 650 | 0.083219 | 0.32289 | 0.072005 | 0.20555 | 0.84051 | 0.043203 | 0.55756 | 14.5 | 56.26 | 0.00041325 | 35.815 | 146.45 | 0.00024795 | 97.15 | 1*323/75 ACSR | 145 | [6 empty] | 906 | 909 | 0 | 0 |  |  |  |  | 55كم قنا+90كم الاقصر |  |  | 0.083219 | 0.32289 | 0.072005 | 0.20555 | 0.84051 | 0.043203 | 0.55756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ادفو | اسنا | IDFO | ISNA | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 58 | 600/5 | 600/5 | 600 | 137.1744 | 650 | 0.033287 | 0.12916 | 0.028802 | 0.08222 | 0.3362 | 0.017281 | 0.22303 | 5.8 | 22.504 | 0.0001653 | 14.326 | 58.58 | 9.918e-05 | 38.86 | 1*323/75 ACSR | 58 | [6 empty] | 905 | 906 | 0 | 0 |  |  |  |  | 23كم ادفو + 35كم الاقصر |  |  | 0.033287 | 0.12916 | 0.028802 | 0.08222 | 0.3362 | 0.017281 | 0.22303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ادفو | اسنا | IDFO | ISNA | مصر العليا | Circuit | 2 | 132 | 1*323/75 ACSR | 58 | 600/5 | 600/5 | 600 | 137.1744 | 650 | 0.033287 | 0.12916 | 0.028802 | 0.08222 | 0.3362 | 0.017281 | 0.22303 | 5.8 | 22.504 | 0.0001653 | 14.326 | 58.58 | 9.918e-05 | 38.86 | 1*323/75 ACSR | 58 | [6 empty] | 905 | 906 | 0 | 0 |  |  |  |  | 23كم ادفو + 35كم الاقصر |  |  | 0.033287 | 0.12916 | 0.028802 | 0.08222 | 0.3362 | 0.017281 | 0.22303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كوم امبو | ادفو | KOMOMBO | IDFO | مصر العليا | Circuit | 1 | 132 | 1*323/75 ACSR | 62.5 | 600/5 | 600/1 | 600 | 137.1744 | 650 | 0.03587 | 0.13918 | 0.031037 | 0.088599 | 0.36229 | 0.018622 | 0.24033 | 6.25 | 24.25 | 0.00017813 | 15.4375 | 63.125 | 0.00010687 | 41.875 | 1*323/75 ACSR | 62.5 | [6 empty] | 903 | 905 | 0 | 0 | [7 empty] | 0.03587 | 0.13918 | 0.031037 | 0.088599 | 0.36229 | 0.018622 | 0.24033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الفيروسيليكون | ادفو | FEROSLKN | IDFO | مصر العليا | Circuit | 1 | 132 | 1*380/88 ACSR | 3 | 600/5 | 600/5 | 600 | 137.1744 | 670 | 0.0014377 | 0.0068871 | 0.0014898 | 0.0051653 | 0.016357 | 0.0011657 | 0.010158 | 0.2505 | 1.2 | 8.55e-06 | 0.9 | 2.85 | 6.69e-06 | 1.77 | 1*380/88 ACSR | 3 | [6 empty] | 904 | 905 | 0 | 0 | [7 empty] | 0.0014377 | 0.0068871 | 0.0014898 | 0.0051653 | 0.016357 | 0.0011657 | 0.010158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الفيروسيليكون | ادفو | FEROSLKN | IDFO | مصر العليا | Circuit | 2 | 132 | 1*380/88 ACSR | 3 | 600/5 | 600/5 | 600 | 137.1744 | 670 | 0.0014377 | 0.0068871 | 0.0014898 | 0.0051653 | 0.016357 | 0.0011657 | 0.010158 | 0.2505 | 1.2 | 8.55e-06 | 0.9 | 2.85 | 6.69e-06 | 1.77 | 1*380/88 ACSR | 3 | [6 empty] | 904 | 905 | 0 | 0 | [7 empty] | 0.0014377 | 0.0068871 | 0.0014898 | 0.0051653 | 0.016357 | 0.0011657 | 0.010158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
كوم امبو | الفيروسيليكون | KOMOMBO | FEROSLKN | مصر العليا | Circuit | 1 | 132 | 1*326/62.5 ACSR | 76 | 800/5 | 800/5 | 600 | 137.1744 | 650 | 0.043618 | 0.16924 | 0.03774 | 0.10774 | 0.44054 | 0.022644 | 0.29224 | 7.6 | 29.488 | 0.0002166 | 18.772 | 76.76 | 0.00012996 | 50.92 | 1*326/62.5 ACSR | 76 | [6 empty] | 903 | 904 | 0 | 0 | [7 empty] | 0.043618 | 0.16924 | 0.03774 | 0.10774 | 0.44054 | 0.022644 | 0.29224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
الاقصر شرق | جنوب قنا | LXR-SHRQ | SOTH-QUENA | مصر العليا | Circuit | 1 | 132 | 1*323/77 ACSR | 57 | 800/1 | 500/1 | 500 | 114.312 | 650 | 0.032713 | 0.12693 | 0.028305 | 0.080802 | 0.33041 | 0.016983 | 0.21918 | 5.7 | 22.116 | 0.00016245 | 14.079 | 57.57 | 9.747e-05 | 38.19 | 1*323/77 ACSR | 57 | [6 empty] | 908 | 909 | 0 | 0 | [7 empty] | 0.032713 | 0.12693 | 0.028305 | 0.080802 | 0.33041 | 0.016983 | 0.21918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | نجع حمادي | SOTH-QUENA | NAG-HAM | مصر العليا | Circuit | 1 | 132 | 1*400/70 ACO | 46.2 | 500/1 | 750/1 | 500 | 114.312 | 750 | 0.021212 | 0.10394 | 0.022942 | 0.079545 | 0.25189 | 0.013765 | 0.15644 | 3.696 | 18.1104 | 0.00013167 | 13.86 | 43.89 | 7.9002e-05 | 27.258 | 1*400/70 ACO | 46.2 | [6 empty] | 909 | 911 | 0 | 0 | [7 empty] | 0.021212 | 0.10394 | 0.022942 | 0.079545 | 0.25189 | 0.013765 | 0.15644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | نجع حمادي | SOTH-QUENA | NAG-HAM | مصر العليا | Circuit | 2 | 132 | 1*400/70 ACO | 46.2 | 500/1 | 750/1 | 500 | 114.312 | 750 | 0.021212 | 0.10394 | 0.022942 | 0.079545 | 0.25189 | 0.013765 | 0.15644 | 3.696 | 18.1104 | 0.00013167 | 13.86 | 43.89 | 7.9002e-05 | 27.258 | 1*400/70 ACO | 46.2 | [6 empty] | 909 | 911 | 0 | 0 | [7 empty] | 0.021212 | 0.10394 | 0.022942 | 0.079545 | 0.25189 | 0.013765 | 0.15644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 1 | 132 | 1*392/50 ACSR | 2.8 | 750/1 | 750/1 | 750 | 171.468 | 750 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 1.064 | 2.66 | 4.788e-06 | 1.652 | 1*392/50 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 2 | 132 | 1*392/50 ACSR | 2.8 | 750/1 | 750/1 | 750 | 171.468 | 750 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 1.064 | 2.66 | 4.788e-06 | 1.652 | 1*392/50 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 3 | 132 | 1*392/50 ACSR | 2.8 | 750/1 | 750/1 | 750 | 171.468 | 750 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 1.064 | 2.66 | 4.788e-06 | 1.652 | 1*392/50 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 4 | 132 | 1*392/50 ACSR | 2.8 | 750/1 | 750/1 | 750 | 171.468 | 750 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 1.064 | 2.66 | 4.788e-06 | 1.652 | 1*392/50 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0061065 | 0.015266 | 0.00083426 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 5 | 132 | 1*380/88 ACSR | 2.8 | 750/1 | 750/1 | 670 | 153.1781 | 670 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0048209 | 0.015266 | 0.001088 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 0.84 | 2.66 | 6.244e-06 | 1.652 | 1*380/88 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0048209 | 0.015266 | 0.001088 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | الالمنيوم | NAG-HAM | ALUMINUM | مصر العليا | Circuit | 6 | 132 | 1*380/88 ACSR | 2.8 | 750/1 | 750/1 | 670 | 153.1781 | 670 | 0.0013418 | 0.0064279 | 0.0013904 | 0.0048209 | 0.015266 | 0.001088 | 0.0094812 | 0.2338 | 1.12 | 7.98e-06 | 0.84 | 2.66 | 6.244e-06 | 1.652 | 1*380/88 ACSR | 2.8 | [6 empty] | 911 | 913 | 0 | 0 | [7 empty] | 0.0013418 | 0.0064279 | 0.0013904 | 0.0048209 | 0.015266 | 0.001088 | 0.0094812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | سوهاج | NAG-HAM | SOHAG | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 100 | 750/1 | 750/1 | 300 | 68.5872 | 300 | 0.15496 | 0.24105 | 0.047393 | 0.41896 | 0.73462 | 0.029795 | 0.43618 | 27 | 42 | 0.000272 | 73 | 128 | 0.000171 | 76 | 1*120/21 ACSR | 100 | [6 empty] | 911 | 914 | 0 | 0 |  |  |  |  | 50كم بقنا + 50كم سوهاج |  |  | 0.15496 | 0.24105 | 0.047393 | 0.41896 | 0.73462 | 0.029795 | 0.43618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
نجع حمادي | سوهاج | NAG-HAM | SOHAG | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 100 | 750/1 | 750/1 | 300 | 68.5872 | 300 | 0.15496 | 0.24105 | 0.047393 | 0.41896 | 0.73462 | 0.029795 | 0.43618 | 27 | 42 | 0.000272 | 73 | 128 | 0.000171 | 76 | 1*120/21 ACSR | 100 | [6 empty] | 911 | 914 | 0 | 0 |  |  |  |  | 50كم بقنا + 50كم سوهاج |  |  | 0.15496 | 0.24105 | 0.047393 | 0.41896 | 0.73462 | 0.029795 | 0.43618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوهاج | اسيوط البخارية | SOHAG | ASYOTGEN | مصر العليا | Circuit | 1 | 132 | 1*120/21 ACSR | 94 | 600/5 | 300/1 | 300 | 68.5872 | 300 | 0.14566 | 0.22658 | 0.04455 | 0.39382 | 0.69054 | 0.028007 | 0.41001 | 25.38 | 39.48 | 0.00025568 | 68.62 | 120.32 | 0.00016074 | 71.44 | 1*120/21 ACSR | 94 | [6 empty] | 914 | 920 | 0 | 0 |  |  |  |  | 54كم سوهاج + 40كم مصر الوسطى |  |  | 0.14566 | 0.22658 | 0.04455 | 0.39382 | 0.69054 | 0.028007 | 0.41001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
سوهاج | اسيوط البخارية | SOHAG | ASYOTGEN | مصر العليا | Circuit | 2 | 132 | 1*120/21 ACSR | 94 | 600/5 | 300/1 | 300 | 68.5872 | 300 | 0.14566 | 0.22658 | 0.04455 | 0.39382 | 0.69054 | 0.028007 | 0.41001 | 25.38 | 39.48 | 0.00025568 | 68.62 | 120.32 | 0.00016074 | 71.44 | 1*120/21 ACSR | 94 | [6 empty] | 914 | 920 | 0 | 0 |  |  |  |  | 54كم سوهاج + 40كم مصر الوسطى |  |  | 0.14566 | 0.22658 | 0.04455 | 0.39382 | 0.69054 | 0.028007 | 0.41001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | جنوب قنا | QUENA-S | QUENA-S | مصر العليا | Circuit | 1 | 132 | 2*380/50 ACSR | 0.8 | 500/1 | 500/1 | 500 | 114.312 | 1200 | 0.00018916 | 0.0013866 | 0.00051854 | 0.00050505 | 0.0043618 | 0.00031084 | 0.0027089 | 0.03296 | 0.2416 | 2.976e-06 | 0.088 | 0.76 | 1.784e-06 | 0.472 | 2*380/50 ACSR | 0.8 | [8 empty] | 0 | 0 |  |  |  |  | كل دائرة موصلة على محول من المحولين جهد 220/132 ك ف بجنوب قنا |  |  | 0.00018916 | 0.0013866 | 0.00051854 | 0.00050505 | 0.0043618 | 0.00031084 | 0.0027089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
جنوب قنا | جنوب قنا | QUENA-S | QUENA-S | مصر العليا | Circuit | 2 | 132 | 2*380/50 ACSR | 0.8 | 500/1 | 500/1 | 500 | 114.312 | 1200 | 0.00018916 | 0.0013866 | 0.00051854 | 0.00050505 | 0.0043618 | 0.00031084 | 0.0027089 | 0.03296 | 0.2416 | 2.976e-06 | 0.088 | 0.76 | 1.784e-06 | 0.472 | 2*380/50 ACSR | 0.8 | [8 empty] | 0 | 0 |  |  |  |  | كل دائرة موصلة على محول من المحولين جهد 220/132 ك ف بجنوب قنا |  |  | 0.00018916 | 0.0013866 | 0.00051854 | 0.00050505 | 0.0043618 | 0.00031084 | 0.0027089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | ربط الخزان | A-DAM | A-DAM | مصر العليا | Circuit | 1 | 132 | 1*380/88 ACSR | 0.7 | 750/1 | 750/1 | 500 | 114.312 | 670 | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0.05845 | 0.28 | 1.995e-06 | 0.21 | 0.665 | 1.561e-06 | 0.413 | 1*380/88 ACSR | 0.7 | [8 empty] | 0 | 0 |  |  |  |  | كل دائرة موصلة على محول من المحولات جهد 220/132 ك ف بمحطة ربط الخزان |  |  | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | ربط الخزان | A-DAM | A-DAM | مصر العليا | Circuit | 2 | 132 | 1*380/88 ACSR | 0.7 | 750/1 | 750/1 | 500 | 114.312 | 670 | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0.05845 | 0.28 | 1.995e-06 | 0.21 | 0.665 | 1.561e-06 | 0.413 | 1*380/88 ACSR | 0.7 | [8 empty] | 0 | 0 |  |  |  |  | كل دائرة موصلة على محول من المحولات جهد 220/132 ك ف بمحطة ربط الخزان |  |  | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ربط الخزان | ربط الخزان | A-DAM | A-DAM | مصر العليا | Circuit | 3 | 132 | 1*380/88 ACSR | 0.7 | 750/1 | 750/1 | 500 | 114.312 | 670 | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0.05845 | 0.28 | 1.995e-06 | 0.21 | 0.665 | 1.561e-06 | 0.413 | 1*380/88 ACSR | 0.7 | [8 empty] | 0 | 0 |  |  |  |  | كل دائرة موصلة على محول من المحولات جهد 220/132 ك ف بمحطة ربط الخزان |  |  | 0.00033546 | 0.001607 | 0.00034761 | 0.0012052 | 0.0038166 | 0.00027199 | 0.0023703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LnLst
Lines Parameter Source
KV | Conductor Type List | Parameters in Ohm/KM and for B Mho/KM | [6 empty] | SIL [MW] | Capacity [A] | Note
|  | R1 | X1 | B1*10-6 | R0 | X0 | B0*10-6 | Xm
500 | 4*495/65 ACSR | 0.01703 | 0.27647 | 4.2212 | 0.16448 | 0.87162 | 2.6576 | 0.19839 | 976.8612
500 | 4*490/65 ACSR | 0.01703 | 0.27647 | 4.2212 | 0.16448 | 0.87162 | 2.6576 | 0.19839 | 976.8612
500 | 4*506 AAAC | 0.01703 | 0.27647 | 4.2212 | 0.16448 | 0.87162 | 2.6576 | 0.19839 | 976.8612 |  | . لم يتم التأكد من ان 4*506 مثل 4*490
500 | 3*506 AAAC | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*495/65 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*490/70 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*490/65 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*482/70 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*482/59.7 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602
500 | 3*380/50 ACSR | 0.0217 | 0.295 | 3.96 | 0.247 | 0.78 | 2.92 | 0.23 | 915.9602 |  | غير معلوم الباراميتر لهذا النوع من الموصل
220 | 2*507 AAAC | 0.037 | 0.298 | 3.76 | 0.38 | 0.95 | 2.23 | 0.59 | 171.9219
220 | 2*500 AAAC | 0.037 | 0.298 | 3.76 | 0.38 | 0.95 | 2.23 | 0.59 | 171.9219
220 | 2*380/88 ACSR | 0.0412 | 0.302 | 3.72 | 0.11 | 0.95 | 2.23 | 0.59 | 169.8687
220 | 2*380/80 ACSR | 0.0412 | 0.302 | 3.72 | 0.11 | 0.95 | 2.23 | 0.59 | 169.8687
220 | 2*380/50 ACSR | 0.0412 | 0.302 | 3.72 | 0.11 | 0.95 | 2.23 | 0.59 | 169.8687
220 | 2*405 AAAC | 0.0499 | 0.306 | 3.25 | 0.13 | 0.83 | 2.23 | 0.59 | 157.7344
220 | 2*236 AAAC | 0.0699 | 0.3115 | 3.61 | 0.23 | 0.95 | 2.23 | 0.59 | 164.7669
220 | 2*240/40 ACO | 0.078 | 0.41 | 2.73 | 0.23 | 0.95 | 2.23 | 0.59 | 124.892
220 | 2*240/44 ACO | 0.078 | 0.41 | 2.73 | 0.23 | 0.95 | 2.23 | 0.59 | 124.892
220 | 1*392/50 ACSR | 0.0835 | 0.4 | 2.85 | 0.38 | 0.95 | 1.71 | 0.59 | 129.1926
220 | 1*380/88 ACSR | 0.0835 | 0.4 | 2.85 | 0.3 | 0.95 | 2.23 | 0.59 | 129.1926
220 | 1*380/50 ACSR | 0.0835 | 0.4 | 2.85 | 0.3 | 0.95 | 2.23 | 0.59 | 129.1926
220 | 1*506 AAAC | 0.0825 | 0.418 | 2.72 | 0.3 | 0.95 | 2.23 | 0.59 | 123.4644
220 | 1*405 AAAC | 0.0825 | 0.418 | 2.72 | 0.3 | 0.95 | 2.23 | 0.59 | 123.4644
220 | 1*454 AAAC | 0.0726 | 0.4 | 2.72 | 0.3 | 0.95 | 2.23 | 0.59 | 126.2118
220 | 1*400/70 ACO | 0.08 | 0.392 | 2.85 | 0.3 | 0.95 | 1.71 | 0.59 | 130.5043
220 | 1*326/62.5 ACSR | 0.1 | 0.388 | 2.85 | 0.247 | 1.01 | 1.71 | 0.67 | 131.1753
220 | 1*323/75 ACSR | 0.1 | 0.388 | 2.85 | 0.247 | 1.01 | 1.71 | 0.67 | 131.1753
220 | 1*323/77 ACSR | 0.1 | 0.388 | 2.85 | 0.247 | 1.01 | 1.71 | 0.67 | 131.1753
220 | 1*240 AAAC | 0.119 | 0.4 | 2.85 | 0.73 | 1.28 | 1.71 | 0.76 | 129.1926 |  | غير معلوم البيانات لهذا الموصل
220 | 1*235.6 AAAC | 0.119 | 0.4 | 2.85 | 0.73 | 1.28 | 1.71 | 0.76 | 129.1926 |  | غير معلوم البيانات لهذا الموصل
220 | 1*120/21 ACSR | 0.27 | 0.42 | 2.72 | 0.73 | 1.28 | 1.71 | 0.76 | 123.1701
220 | THERMAL 2*357/54 ACSS/TW ,728kcmil | 0.035591 | 0.34123 | 3.3714 | 0.26137 | 1.0274 | 2.3461 | 0.22872 | 152.1339 |  | PUFFIN/ACSS/TW | 1 | تم حسابه ب line prop
220 | Thermal Double 2*255/98 | 0.057262 | 0.33759 | 3.3651 | 0.28207 | 1.1782 | 2.096 | 0.77578 | 152.8105
220 | Thermal Double Stacir 2*238/97 | 0.057262 | 0.33759 | 3.3651 | 0.28207 | 1.1782 | 2.096 | 0.77578 | 152.8105
220 | Thermal double 2*255/88 | 0.057262 | 0.33759 | 3.3651 | 0.28207 | 1.1782 | 2.096 | 0.77578 | 152.8105
220 | Thermal Double 2*255/98 ACSS | 0.057262 | 0.33759 | 3.3651 | 0.28207 | 1.1782 | 2.096 | 0.77578 | 152.8105
220 | Thermal 1*439/46 GT A.C.S.R | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277
220 | Thermal Invar 431 mm | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277 |  | غير معلوم الباراميتر لهذا النوع من الموصل الحراري
220 | Thermal 1*290/88 | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277 |  | غير معلوم الباراميتر لهذا النوع من الموصل الحراري
220 | Thermal 1*290/88 | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277 |  | غير معلوم الباراميتر لهذا النوع من الموصل الحراري
220 | Thermal Invar 1*255/88 | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277 |  | غير معلوم الباراميتر لهذا النوع من الموصل الحراري
220 | Thermal Stacir 1*238/97 | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277
220 | Thermal Invar 1*238/97 | 0.11417 | 0.44204 | 2.5953 | 0.33897 | 1.2826 | 1.7413 | 0.77577 | 117.277
220 | THERMAL 1*357/54 ACSS/TW ,728kcmil | 0.07077 | 0.43583 | 2.6526 | 0.29655 | 1.122 | 1.9232 | 0.22873 | 119.4046
220 | 1*375.2/87 MCM 740 | 0.07385 | 0.5947 | 7.44 | 0.752 | 1.88 | 4.415 | 1.168 | 171.1918
220 | 1*375.2/87 MCM 461 | 0.07385 | 0.5947 | 7.44 | 0.752 | 1.88 | 4.415 | 1.168 | 171.1918 |  | غير معلوم الباراميتر لهذا النوع من الموصل الحراري
220 | XLPE 2500mm2 | 0.01287 | 0.16835 | 71.62 | 0.15374 | 0.10498 | 60 | 0 | 998.2883 |  | غير معلوم بيانات الكابل
220 | XLPE 2000mm2 Elswedy | 0.01287 | 0.16835 | 71.62 | 0.15374 | 0.10498 | 60 | 0 | 998.2883
220 | XLPE 2000mm2 Elswedy energy | 0.01287 | 0.16835 | 72.25 | 0.15374 | 0.0637 | 60 | 0 | 1002.6693
220 | XLPE 1600mm2 Elswedy | 0.0121 | 0.1215 | 44 | 0.2054 | 0.0714 | 53 | 0 | 921.0508
220 | XLPE 1600mm2 ELSEWEDY CABLES | 0.01554 | 0.175 | 66.31 | 0.1856 | 0.1084 | 56.86 | 0 | 942.1409 |  | manual no 2
220 | XLPE 1600mm2 Energya | 0.01553 | 0.176 | 67.25 | 0.181 | 0.1074 | 57.67 | 0 | 946.0959 |  | manual no 1
220 | 2*XLPE 1600mm2 Elswedy (every circuit two cable in parralel) | 0.00605 | 0.06075 | 88 | 0.1027 | 0.0357 | 106 | 0 | 1842.1015
220 | CableHi-Pr kanda1267 | 0.02 | 0.1344 | 88 | 0.08 | 0.13 | 66 | 0 | 1238.4745
220 | Cable Hi-Pr Dilion 1267 | 0.028 | 0.129 | 128.8053 | 0.18169 | 0.283 | 64.8 | 0 | 1529.3869
220 | XLPE1200HDPECABLE | 0.01616 | 0.184 | 59.4 | 0.172 | 0.0737 | 53 | 0 | 869.6203
220 | XLPE 1200mm2 | 0.0157 | 0.1996 | 62 | 0.202 | 0.07 | 52 | 0 | 853.0234
220 | XLPE 1200mm2 Elswedy energy | 0.02107 | 0.1683 | 60.63 | 0.2195 | 0.0751 | 52 | 0 | 918.6437
220 | Giza XLPE 1200 | 0.0162 | 0.18 | 60.63 | 0.2315 | 0.0714 | 64.8 | 0 | 888.2862
220 | CABLE 1*1200 | 0.0151 | 0.175 | 100 | 0.07 | 0.2 | 53 | 0 | 1156.9813
220 | XLPE1000HDPECABLE | 0.01616 | 0.184 | 59.4 | 0.172 | 0.0737 | 53 | 0 | 869.6203
220 | XLPE1000mm2 | 0.0176 | 0.124 | 57.5 | 0.21 | 0.08 | 50 | 0 | 1042.2417
220 | CableHpofc 850 | 0.02429 | 0.184 | 84.823 | 0.24758 | 0.06459 | 55 | 0 | 1039.186
220 | Two Cable in Parralel of Cable L-Pr Brilli800 | 0.01105 | 0.0925 | 176 | 0.1235 | 0.46 | 129.6 | 0 | 2111.2071
220 | Cable L-Pr Brilli800 | 0.0221 | 0.185 | 88 | 0.247 | 0.92 | 64.8 | 0 | 1055.6035
220 | Cable cu oil f 1*800 | 0.0221 | 0.19 | 76.969 | 0.331 | 0.28 | 70 | 0 | 974.1516 |  | تم تعديل قيمة مقاومة الكابل الصيني من 0.221 اوم /كم الى 0.0221 مطلوب التاكد من القيمة الجديدة . قيمة المقاومة القديمة كبيرة جدا
220 | CABLE 1*800 | 0.0202 | 0.1344 | 88 | 0.08 | 0.13 | 60 | 0 | 1238.4745
220 | XLPE 1*400 cable | 0.0151 | 0.3729 | 58.842 | 0.1727 | 0.0743 | 50 | 0 | 607.9852
220 | Gas Insulated Busbar (Zero Branch) | 0.0157 | 0.1996 | 62 | 0.202 | 0.07 | 52 | 0 | 853.0234

## Trans_220_mob (hidden)
Arabic Station Name | English Station Name | ID | Nominal Voltage [KV] |  |  | Rating [MVA] |  |  | REACTANCES [P.U] |  |  | Base [MVA] | Tap Changer |  |  |  | Full Load Losses [KW] | Resistance R [Refer to High Wind] |  | Manufacture | Zone | PSSE No. |  |  | Online System Station Name | File No.
[13 empty] | No of Steps | First Tap [KV] | Last Tap [KV] | Neut. Tap No
|  |  | H | M | L | H | M | L | XHM | XHL | XML | [6 empty] | [Ohm] | [P.U] |  |  | Fr | To | Tr
راس سدر | Ras-Sedr | 1 | 220 | 66 | 11 | 40 | 40 | 15 | 0.1494 | 0.0509 | 0.2076 | 40 | 17 | 242 | 198 | 9 | 230000 | 6.9575 | 0.00575 | Mobile Trans | Canal |  |  |  | RASSEDR
الطور | El Tor | 1 | H: 220; M: 11; H: 75 | 75 | [5 empty] | 0 | 0 |  | Canal
الطور | El Tor | 2 | H: 220; M: 11; H: 33.2; XHM: 0.1287 | 33.2 | 9 |  |  |  |  | 0 | 0 | BBC | Canal
صان الحجر | SANHAGAR (MOBILE) | 1 | 220 | 72.3 | 12 | 40 | 40 | 15 | 0.1446 | 0.1512 | 0.31573 | 40 | 17 | 242 | 190 | 9 |  | 0 | 0 | سيمنز | Canal
زويل سابقا | Zewal (MOBILE)سابقا | 1 | 220 | 24 | 24 | 125 | 62.5 | 62.5 | 0.139 |  |  | 125 | 17 | 242 | 198 | 9a,b,c | 381400 | 1.1814 | 0.0030512 | getra | Cairo
المساعيد سابقا | MASAED | 1 | 220 | 70 | 11.5 | 40 | 40 | 15 | 0.1474 | 0.056 | 0.2065 | 40 | 17 | 242 | 198 | 9A |  | 0 | 0 | Mitsubishi | Canal |  |  |  | MESAAEED
المساعيد سابقا | MASAED | 2 | 220 | 70 | 11.5 | 40 | 40 | 15 | 0.1449 | 0.056 | 0.2065 | 40 | 17 | 242 | 198 | 9A |  | 0 | 0 | Mitsubishi | Canal |  |  |  | MESAAEED
المساعيد سابقا | MASAED | 3 | 220 | 70 | 11.5 | 40 | 40 | 15 | 0.1458 | 0.0504 | 0.2027 | 40 | 17 | 242 | 198 | 9A |  | 0 | 0 | Mitsubishi | Canal |  |  |  | MESAAEED

## notes (hidden)
التاريخ | الملاحظة
ادخال بيانات المحول 2 بالدخيلة وباقي المحولات بالمحطة
2022-06-29 | افاد م مصطفى عبد الحسيب من مشروعات كابلات القاهرة في يوم 24 مارس 2022 انه لم ينته بعد ادخال كابلات في دوائر الجمال / اكتوبر والهضبة / اكتوبر و و 12 كم من القاهرة 500 / اكتوبر
مطلوب الورق الرسمي الذي ارسله المهندس اشرف لطفي و م اياد من خطوط القناة بخصوص سعة خط اسمنت المصرية / الكوستيل
2022-12-24 | يوجد خطة لانشاء دائرتي توشكى 2 / توشكى 4 رقم 3 و 4 ولم يتم البدا بعد افاد بذلك م محمد حامد خطوط اسوان يوم 12/24/2022
2022-12-20 | ينتظر دخول المحول الثالث بمحطة بني سويف الصناعية قدرة 175 م ف ا السويدي تم الاتصال بالمحطة يوم 12/20/2022وافادت انه لم يتم توريد المحول الثالث بعد
2022-10-02 | ينتظر دخول محول جديد بمحطة عروق الصلب لزيادة احمال المحطة . افادت المحطة يوم 12/12/2022 انه يتوقع دخول المحول الجديد خلال سته اشهر
2022-10-15 | متنقلتي محطة دمو قدرة 2*75 م ف ا . واحد منهم في مخزن المحطة والاخر تم نقله الى اسيوط مطلوب السؤال عن مكان تركيبه بالضبط
2022-12-18 | دخول محول قريبا في سفاجا رقم 2 بدل المحول المتهالك قدرة 75 م ف ا AEG والمحول الجديد قدرة 125 م ف ا منقول من سمالوط كان رقم 8 السويدي
2022-12-22 | افاد م محمد طه من مشروعات كابلات القاهرة في يوم 22 ديسمبر 2022 انه لم ينته بعد من عمل كابلات في دوائر الهضبة / اكتوبردخولا على محطة الخمائل الجديدة و وجاري العمل في كابل طوله 7 كم من القاهرة 500 / اكتوبروتم الغاء مشروع كابلات في دوائر الجمال / اكتوبر وافاد ايضا ان الكابلين المتوازيان الزيتي في دائرة جنوب المعادي / عين الصيرة رقم 1 جاري احلالهما بكابل 1*1600
2023-02-04 | المحولات في الشبكة كل الجهود ( 500 و 220 و 132 و 66 ) موصلة ستار بينما الجهود الاقل من 66 موصلة دلتا ماعدا المحول 1 في عروق الصلب جهد 220/33/6.9 قدرة 105/90/15 م ف ا .نجد ان الملف جهد 33 ك ف موصل ستار ومحولي اللاهون و محولي المقطم ومحولي الجمال قدرة 75/75/25 م ف ا و جهد 220/24/24 ك ف واحد من الملفين جهد 24 ك ف Y وسعته 75 م ف ا والاخر دلتا وسعته 25 م ف ا
2023-02-05 | جاري نقل المحول جهد 500/220 ك ف نوع سيمنز بمحطة بنبان 3 الذي كان مركب على دائرة السد العالي / نجع حمادي الى محطة زهراء المعادي غالبا وذلك لزيادة تحميل المحولات العاملة وللمحول المنقول نفس الجهد وimpedance لمحولات زهراء المعادي